## Inputs
Base Assumptions
Discount rate | 7%
Reactor asset life (years) | 30
Capacitor asset life (years) | 20
SVC asset life (years) | 30
BESS asset life (years) | 20
O&M | 1%
Sensitivities | Low | High
Cost | 70% | 130%
Discount rate | 3% | 10.5%
Reasonable scenarios |  |  | POEs
Scenario | Weighting |  | POE | Weighting
Step Change | 43% |  | POE90 | 30.4%
Green Energy Exports | 15% |  | POE50 | 39.2%
Progressive Change | 42% |  | POE10 | 30.4%

## Do Nothing Costs
Do nothing Pillar 1 | Weighted outcomes
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Max supportable demand DPTS (MW) | 281.729 | 288.981 | 287.1606 | 284.3604 | 290.23 | 289.9399 | 288.6801 | 277.5299 | 273.7406 | 269.9892
Max supportable demand TBTS, CBTS (MW) | 1185.543 | 1246.297 | 1221.5812 | 1064.6928 | 1120.263 | 1162.7518 | 1122.1913 | 1032.345 | 938.6077 | 938.3143
Max supportable demand MTS, HTS, SVTS (MW) | 1566.946 | 1616.332 | 1636.7391 | 1591.4791 | 1511.704 | 1572.8588 | 1522.9852 | 1401.6677 | 1275.3135 | 1232.2071
USE (MWhrs) | 0 | 0 | 0.32955 | 1.2425 | 2.2881 | 7.5309 | 16.8878 | 42.3016 | 224.8874 | 483.6683
Hours over limit (hrs) | 0 | 0 | 0.045 | 0.1095 | 0.1845 | 0.5445 | 1.0805 | 3.662 | 14.386 | 31.3535
USE costs ($) | 0 | 0 | 0.015869 | 0.059829 | 0.11018 | 0.36263 | 0.81319 | 2.0369 | 10.8289 | 23.2898
VER cost($) | 0 | 0 | -1.7689e-05 | -7.0027e-05 | -0.00013663 | -0.00048002 | -0.0011897 | -0.0032356 | -0.01871 | -0.04381
Do nothing Pillar 2 | Weighted outcomes
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Gas gen fuel cost ($/MWh) | 223.4119 | 192.9278 | 171.8486 | 170.343 | 169.3414 | 170.0597 | 171.5472 | 171.8864 | 173.0494 | 176.4299
Opex ($/MWh) | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186 | 10.1186
Out of merit order dispatch (MWh) | 0 | 0 | 606.2697 | 6977.6709 | 21739.0171 | 41389.4926 | 65120.1257 | 64813.8857 | 83334.2149 | 89279.696
Out of merit order start-up costs ($M) | 0 | 0 | 0.0038828 | 0.043683 | 0.13495 | 0.25632 | 0.40535 | 0.40268 | 0.51821 | 0.56979
Out of merit order dispatch costs ($M) | 0 | 0 | 0.1098 | 1.2353 | 3.816 | 7.2482 | 11.4622 | 11.387 | 14.6536 | 16.1122
Displaced gen dispatch costs ($M) | 0 | 0 | 0.0021385 | 0.022599 | 0.080731 | 0.15435 | 0.24159 | 0.24077 | 0.29956 | 0.31109
Total costs associated with out of merit order dispatch of gas gen ($M) | 0 | 0 | 0.11154 | 1.2563 | 3.8702 | 7.3501 | 11.626 | 11.5489 | 14.8723 | 16.3709
Out of merit order dispatch emissions (tonne) | 0 | 0 | 409.9119 | 4664.2799 | 14473.0917 | 27499.0015 | 43118.8448 | 42683.0931 | 54586.7936 | 58301.3726
Displaced gen dispatch emissions (tonne) | 0 | 0 | 178.289 | 1884.0965 | 6730.7077 | 12868.6971 | 20142.2066 | 20073.3953 | 24974.8069 | 25935.8695
VER ($/kg) | 0.075 | 0.08 | 0.084 | 0.089 | 0.095 | 0.105 | 0.114 | 0.124 | 0.135 | 0.146
Emissions costs associated with out of merit order dispatch of gas gen ($M) | 0 | 0 | 0.019456 | 0.24744 | 0.73553 | 1.5362 | 2.6193 | 2.8036 | 3.9976 | 4.7254

## Option 1
Option 1
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
[6 empty] | 3x reactors |  | 1x DPTS cap |  |  | 2x EM caps
Capacity MVAr |  | 2029: 300; 2031: 100; 2034: 200; 2051: -100; 2054: -200; 2059: -300
Capital Cost $M |  | 2029: 25.8672; 2031: 6.9285; 2034: 12.788; 2051: -6.9285; 2054: -12.788; 2059: -25.8672
Annual Cost $M |  | 2029: 1.9482; 2031: 0.61121; 2034: 1.1281; 2051: -0.61121; 2054: -1.1281; 2059: -1.9482
O&M $M |  | 2029: 0.019482; 2031: 0.0061121; 2034: 0.011281; 2051: -0.0061121; 2054: -0.011281; 2059: -0.019482
Total P2 capacity |  | 0 | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 0
P2 Gross Market Benefits $M | [5 empty] | 3.8702 | 7.3501 | 11.626 | 11.5489 | 14.8723 | 16.3709 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 0 | 0
P2 Gross VER Benefits $M | [5 empty] | 0.73553 | 1.5362 | 2.6193 | 2.8036 | 3.9976 | 4.7254 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 0 | 0
P2 Gross All Benefits $M | [5 empty] | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
Total P1 capacity |  | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P1 Gross All Benefits $M | [7 empty] | 0.812 | 2.0337 | 10.0474 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 6.1465 | 6.1465 | 6.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summary | NPV | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
P2 Total Cost $M | [5 empty] | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 0
P2 Gross Market Benefits - NPV ($M) | 152.9849 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
P2 Net Market Benefits - NPV ($M) | 134.3576 | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | 12.2777 | 12.3848 | 16.9023 | 19.1286 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 0 | 0
P1 Total Cost $M | [7 empty] | 0.61733 | 0.61733 | 0.61733 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.7567 | 1.1394 | 1.1394 | 1.1394 | 0
P1 Gross Market Benefits - NPV ($M) | 132.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 0.812 | 2.0337 | 10.0474 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 23.1647 | 6.1465 | 6.1465 | 6.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P1 Net Market Benefits - NPV ($M) | 122.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19467 | 1.4164 | 9.4301 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 21.408 | 5.0071 | 5.0071 | 5.0071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Total Cost $M |  | 0 | 0 | 0 | 0 | 1.9677 | 1.9677 | 2.585 | 2.585 | 2.585 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.7244 | 3.1071 | 3.1071 | 3.1071 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 5.4123e-16 | 5.4123e-16
All Gross Market Benefits - NPV ($M) | 285.9344 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 15.0573 | 16.3862 | 28.9173 | 44.261 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 41.271 | 24.2527 | 24.2527 | 24.2527 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
All Net Market Benefits - NPV ($M) | 256.3834 | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | 12.4723 | 13.8012 | 26.3323 | 40.5366 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 37.5466 | 21.1457 | 21.1457 | 21.1457 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | -5.4123e-16 | -5.4123e-16
DPTS = Deer Park Terminal Station
EM = Eastern Metro

## Option 2
Option 2
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
[6 empty] | 3x reactors |  | 1x DPTS cap |  |  | 1x EM caps; EM NNS
Capacity MVAr |  | 2029: 300; 2031: 100; 2034: 100+EM NNS; 2051: -100; 2054: -100 - EM NNS; 2059: -300
Capital Cost $M |  | 2029: 25.8672; 2031: 6.9285; 2034: C; 2051: -6.9285; 2054: C; 2059: -25.8672
Annual Cost $M |  | 2029: 1.9482; 2031: 0.61121; 2034: C; 2051: -0.61121; 2054: C; 2059: -1.9482
O&M $M |  | 2029: 0.019482; 2031: 0.0061121; 2034: C; 2051: -0.0061121; 2054: C; 2059: -0.019482
Total P2 capacity |  | 0 | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 +EM NNS | 300 | 300 | 300 | 300 | 300 | 0
P2 Gross Market Benefits $M | [5 empty] | 3.8702 | 7.3501 | 11.626 | 11.5489 | 14.8723 | 16.3709 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 0 | 0
P2 Gross VER Benefits $M | [5 empty] | 0.73553 | 1.5362 | 2.6193 | 2.8036 | 3.9976 | 4.7254 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 0 | 0
P2 Gross All Benefits $M | [5 empty] | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
Total P1 capacity |  | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 200 +EM NNS | 100 +EM NNS | 100 +EM NNS | 100 +EM NNS | 0 | 0 | 0 | 0 | 0 | 0
P1 Gross All Benefits $M | [7 empty] | 0.812 | 2.0337 | 10.0474 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 5.7745 | 5.7745 | 5.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Summary | NPV | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
P2 Total Cost $M | [5 empty] | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 0 | 0
P2 Gross Market Benefits - NPV ($M) | 152.9849 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
P2 Net Market Benefits - NPV ($M) | C | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | 12.2777 | 12.3848 | 16.9023 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 0 | 0
P1 Total Cost $M | [7 empty] | 0.61733 | 0.61733 | 0.61733 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 0 | 0
P1 Gross Market Benefits - NPV ($M) | 131.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 0.812 | 2.0337 | 10.0474 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 22.8434 | 5.7745 | 5.7745 | 5.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P1 Net Market Benefits - NPV ($M) | C | 0 | 0 | 0 | 0 | 0 | 0 | 0.19467 | 1.4164 | 9.4301 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 0 | 0 | 0 | 0 | 0 | 0 | 0
All Total Cost $M |  | 0 | 0 | 0 | 0 | 1.9677 | 1.9677 | 2.585 | 2.585 | 2.585 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | -7.9103e-16 | -7.9103e-16
All Gross Market Benefits - NPV ($M) | 284.0599 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 15.0573 | 16.3862 | 28.9173 | 43.9397 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 40.9496 | 23.8807 | 23.8807 | 23.8807 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
All Net Market Benefits - NPV ($M) | C | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | 12.4723 | 13.8012 | 26.3323 | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | C | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 7.9103e-16 | 7.9103e-16
C = Confidential
DPTS = Deer Park Terminal Station
EM = Eastern Metro
NNS = Non-network service

## Option 3
Option 3
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
[6 empty] | 3x reactors |  | DPTS NNS |  |  | 1x EM cap
Capacity MVAr |  | 2029: 300; 2031: DPTS; 2034: 100; 2051: -DPTS; 2054: -100; 2059: -300
Capital Cost $M |  | 2029: 25.8672; 2031: 268.8; 2034: 6.394; 2051: -268.8; 2054: -6.394; 2059: -25.8672
Annual Cost $M |  | 2029: 1.9482; 2031: 23.7129; 2034: 0.56406; 2051: -23.7129; 2054: -0.56406; 2059: -1.9482
O&M $M |  | 2029: 0.019482; 2031: 2.4248; 2034: 0.0056406; 2051: -2.4248; 2054: -0.0056406; 2059: -0.019482
Total P2 capacity | [5 empty] | 300 | 300 | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 +DPTS | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0
P2 Gross Market Benefits $M | [5 empty] | 3.8702 | 7.3501 | 11.626 | 11.5489 | 14.8723 | 16.3709 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 0
P2 Gross VER Benefits $M | [5 empty] | 0.73553 | 1.5362 | 2.6193 | 2.8036 | 3.9976 | 4.7254 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 0
P2 Gross All Benefits $M | [5 empty] | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0
Total P1 capacity | [7 empty] | DPTS | DPTS | DPTS | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | DPTS +100 | 100 | 100 | 100 | 0 | 0
P1 Gross All Benefits $M | [7 empty] | 0.812 | 2.0337 | 10.2456 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 3.8368 | 3.8368 | 3.8368 | 0 | 0
Summary | NPV | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
P2 Total Cost $M | [5 empty] | 1.9677 | 1.9677 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 28.1054 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 0
P2 Gross Market Benefits - NPV ($M) | 152.9849 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
P2 Net Market Benefits - NPV ($M) | -50.1548 | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | -13.86 | -13.7529 | -9.2355 | -7.0091 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | -9.9991 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 0 | 0
P1 Total Cost $M | [7 empty] | 26.1377 | 26.1377 | 26.1377 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 26.7074 | 0.5697 | 0.5697 | 0.5697 | 1.9975e-15
P1 Gross Market Benefits - NPV ($M) | 131.0547 | 0 | 0 | 0 | 0 | 0 | 0 | 0.812 | 2.0337 | 10.2456 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 22.9842 | 3.8368 | 3.8368 | 3.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 0
P1 Net Market Benefits - NPV ($M) | -56.7406 | 0 | 0 | 0 | 0 | 0 | 0 | -25.3257 | -24.104 | -15.8921 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | -3.7232 | 3.2671 | 3.2671 | 3.2671 | -1.9975e-15 | 0 | 0 | 0 | 0 | 0 | 0
All Total Cost $M |  | 0 | 0 | 0 | 0 | 1.9677 | 1.9677 | 28.1054 | 28.1054 | 28.1054 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 28.6751 | 2.5374 | 2.5374 | 2.5374 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 1.9677 | 2.5396e-15 | 2.5396e-15
All Gross Market Benefits - NPV ($M) | 284.0396 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 15.0573 | 16.3862 | 29.1155 | 44.0805 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 41.0904 | 21.943 | 21.943 | 21.943 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
All Net Market Benefits - NPV ($M) | 77.617 | 0 | 0 | 0 | 0 | 2.6381 | 6.9187 | -13.0481 | -11.7192 | 1.0101 | 15.4054 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 12.4153 | 19.4056 | 19.4056 | 19.4056 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | 16.1386 | -2.5396e-15 | -2.5396e-15
DPTS = Deer Park Terminal Station
EM = Eastern Metro
NNS = Non-network service

## Option 4
Option 4
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
[6 empty] | 2x reactors 1x SVC |  | 1x DPTS cap
Capacity MVAr |  | 2029: 350; 2031: 100; 2051: -100; 2059: -350
Capital Cost $M |  | 2029: 50.3245; 2031: 6.9285; 2051: -6.9285; 2059: -50.3245
Annual Cost $M |  | 2029: 3.7902; 2031: 0.61121; 2051: -0.61121; 2059: -3.7902
O&M $M |  | 2029: 0.037902; 2031: 0.0061121; 2051: -0.0061121; 2059: -0.037902
Total P2 capacity |  | 0 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 0 | 0
P2 Gross Market Benefits $M | [5 empty] | 3.8702 | 7.3501 | 11.626 | 11.5489 | 14.8723 | 16.3709 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264 | 14.264
P2 Gross VER Benefits $M | [5 empty] | 0.73553 | 1.5362 | 2.6193 | 2.8036 | 3.9976 | 4.7254 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422 | 3.8422
P2 Gross All Benefits $M | [5 empty] | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062
Total P1 capacity |  | 0 | 0 | 0 | 0 | 150 | 150 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0
P1 Gross All Benefits $M | [5 empty] | 0 | 0 | 0.812 | 2.0337 | 10.6201 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551
Summary | NPV | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060
P2 Total Cost $M | [5 empty] | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 0
P2 Gross Market Benefits - NPV ($M) | 152.9849 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 14.2453 | 14.3525 | 18.8699 | 21.0963 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 18.1062 | 0 | 0
P2 Net Market Benefits - NPV ($M) | 116.7454 | 0 | 0 | 0 | 0 | 0.77764 | 5.0583 | 10.4173 | 10.5244 | 15.0418 | 17.2682 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 14.2782 | 0 | 0
P1 Total Cost $M | [5 empty] | 2.5163 | 2.5163 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 3.1336 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 2.5163 | 0
P1 Gross Market Benefits - NPV ($M) | 133.7656 | 0 | 0 | 0 | 0 | 0 | 0 | 0.812 | 2.0337 | 10.6201 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 22.6879 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 5.6551 | 0 | 0
P1 Net Market Benefits - NPV ($M) | 105.5865 | 0 | 0 | 0 | 0 | -2.5163 | -2.5163 | -2.3216 | -1.0999 | 7.4865 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 19.5542 | 3.1388 | 3.1388 | 3.1388 | 3.1388 | 3.1388 | 3.1388 | 3.1388 | 3.1388 | 0 | 0
All Total Cost $M |  | 0 | 0 | 0 | 0 | 3.8281 | 3.8281 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 4.4454 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 3.8281 | 1.0617e-15 | 1.0617e-15
All Gross Market Benefits - NPV ($M) | 286.7506 | 0 | 0 | 0 | 0 | 4.6057 | 8.8863 | 15.0573 | 16.3862 | 29.49 | 43.7842 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 40.7941 | 23.7613 | 23.7613 | 23.7613 | 23.7613 | 23.7613 | 23.7613 | 23.7613 | 23.7613 | 0 | 0
All Net Market Benefits - NPV ($M) | 246.1532 | 0 | 0 | 0 | 0 | 0.77764 | 5.0583 | 10.6119 | 11.9408 | 25.0446 | 39.3388 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 36.3487 | 19.9332 | 19.9332 | 19.9332 | 19.9332 | 19.9332 | 19.9332 | 19.9332 | 19.9332 | -1.0617e-15 | -1.0617e-15
DPTS = Deer Park Terminal Station
EM = Eastern Metro