## Introduction
In December 2018, AER made a final determination on a new Transmission Annual Planning Report (TAPR) Guideline, requiring TNSPs to publish specified information on priority transmission line and terminal station limitations.
The "Summary of Transmission (T) line segment data" spreadsheet provides information on a selected set of transmission lines associated with existing and newly identified DSN priority limitations, based on AEMO’s VAPR and RIT-T reports. As the relevant RIT-Ts are still works in progress, the information provided is subject to change.
The general criteria for selecting the existing assets to be included in the data reporting for priority limitations are:
• The assets which are associated with both load and generation driven priority limitations.
• The preferred option to address the associated priority limitations have not yet been finalised by AEMO or other relevant TNSPs
In addition to the information on priority limitations specified in the TAPR guideline, the "Summary of T. Line Segment data" sheet also includes information related to monitored limitations.
The information on priority and monitored limitations includes:
• Line ID
• Constraint Primary Driver
• From location
• To location
• Reference to Asset Rating
• Voltage level
• Preferred investment-Description (if available)
• Preferred investment- Capital cost (if available)
• Preferred investment -Cost accuracy (if available)
• Preferred investment -Proposed timing (if available)
• Historic line load trace (priority limitations)
• Historic line rating (priority limitations)
Due to file size limitations for web hosting, the data has been split across three files this year:
• Part A - Introduction, Summary of Transmission Line Segment data, Annual Cost of Constraint, Asset Rating
• Part B - Historic Line Loadings
• Part C - Historic Line Ratings

## Summary of T. Line Segment data
VAPR Section Reference | Limitation Type | Victorian Region | Transmission Line ID | Constraint Primary Driver | Location of constraint (start) | Location of constraint (end) | Asset Rating (Load Shed @35°C) | Forecast Demand (note 1) | Voltage Level | Maximum load at risk per year | Energy at risk | Preferred investment - Description (note 4) | Preferred investment - Capital cost (note 4) | Preferred investment - Annual operating cost | Preferred investment — Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MW) | Annual deferral value ($million) | Historic line load trace | Historic line rating | Annual economic cost of constraint | VCR ($/MWh) | Annual constraint duration (note 2) | Constraint duration on peak demand day (note 3)
Appendix A4.1 | Monitored | Central North Corridor | Dederang - Glenrowan 220 kV | Increased demand in regional Victoria and/or increased import from New South Wales. Large-scale new generation connected to Western Victoria and Central North areas, and congestion within Western Victoria relieved to allow the new generation to be sent out of Western Victoria. | 36.454⁰ S 146.991⁰ E | 36.494⁰ S 146.132⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Options considered:- - Install an automatic load shedding and generation runback control scheme to enable the use of five-minute line rating. - Install a wind monitoring scheme. - Install a modular flow controller on the Bendigo – Fosterville – Axedale – Shepparton 220 kV line. - Replace the complete line section with new double-circuit lines. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.1 | Monitored | Central North Corridor | Glenrowan - Shepparton 220 kV |  | 36.494⁰ S 146.132⁰ E | 36.343⁰ S 145.415⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.1 | Monitored | Central North Corridor | Shepparton - Axedale 220 kV |  | 36.343⁰ S 145.415⁰ E | 36.725⁰ S 144.545⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.1 | Monitored | Central North Corridor | Axedale - Fosterville 220 kV |  | 36.494⁰ S 146.132⁰ E | 36.738⁰ S 144.511⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.1 | Monitored | Central North Corridor | Fosterville - Bendigo 220 kV |  | 36.738⁰ S 144.511⁰ E | 36.784⁰ S 144.254⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Sections 4.2.1 and Appendix A4.2 | Priority | Eastern Corridor | Hazelwood – Yallourn 220 kV | Decommissioning of YWPS with modified parallel mode or additional generation is commissioned on the 220 kV network at HWPS, at a site east of HWPS, or on the 500 kV network east of Cranbourne Terminal Station. | 38.273⁰ S 146.392⁰ E | 38.174⁰ S 146.35⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | New switching arrangement at HWPS (modified parallel mode) for post Yallourn retirement to utilise the eastern 220 kV corridor. Minor augmentation project to scope out the details of the works required to facilitate the proposed re-configuration in year 2028. The scope includes minor switching works at HWPS and implementation of a control scheme to manage post contingent overloading. Further thermal capacity can be unlocked through works considered in the East Metro Grid Reinforcement RIT-T | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | 50% | 2028 | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Sections 4.2.1 and Appendix A4.2 | Priority | Eastern Corridor | Rowville - Yallourn 220 kV |  | 37.929⁰ S 145.227⁰ E | 38.174⁰ S 146.35⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR |  | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | 50% | 2028 | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Appendix A4.2 | Monitored (line loading) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Commissioning of additional generation connected at LYPS | 38.281⁰ S 146.428⁰ E | 38.256⁰ S 146.574⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Options Considered: - Construct a new single circuit Hazelwood – Loy Yang 500 kV line. - Construct a new double-circuit Hazelwood – Loy Yang 500 kV and string only one circuit. - Construct a new double-circuit Hazelwood – Loy Yang 500 kV and string both. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.2 | Monitored (line outage window) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Reduction in dispatchable capacity West of Hazelwood 500 kV. Higher and more frequent demands above 6000 MW. | 38.281⁰ S 146.428⁰ E | 38.256⁰ S 146.574⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Options Considered: - Construct a new single circuit Hazelwood – Loy Yang 500 kV line. - Construct a new double-circuit Hazelwood – Loy Yang 500 kV and string only one circuit. - Construct a new double-circuit Hazelwood – Loy Yang 500 kV and string both. System strength and reactive power services to reduce reliance on Loy Yang during low demand periods. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.3 | Monitored | Northern Corridor | Dederang - Mount Beauty 220 kV | Increased import to New South Wales or increased export to New South Wales with high hydro generation in the area | 36.454⁰ S 146.991⁰ E | 36.743⁰ S 147.165⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme and up-rate the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82°C. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Section 4.2.3 and Appendix A4.3 | Monitored | Northern Corridor | Dederang - South Morang 330 kV | Increased import to New South Wales or increased export to New South Wales with high hydro generation in the area | 36.454⁰ S 146.991⁰ E | 37.644⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 330 kV |  |  | Options Consided - Construct additional interconnector to NSW (VNI West) - Change operating voltage of lines to 500 kV - Construct 3rd circuit or replace one circuit with double circuit structures | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.3 | Monitored | Northern Corridor | Mount Beauty - Eildon 220 kV | Increased New South Wales import and export | 36.743⁰ S 147.165⁰ E | 37.224⁰ S 145.921⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Mount Beauty and Eildon to 75°C operation. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Section 4.2.1 and Appendix A4.3 | Priority | Northern Corridor | Eildon - Thomastown 220 kV | Increased demand growth in the Melbourne metropolitan area, which is further exacerbated by changes in how power flows around the network following retirement of YWPS. These changes tend to increase VNI import into Victoria, and thus flow on the Eildon – Thomastown 220 kV line. | 37.224⁰ S 145.921⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | As part of VNI West, cut the Eildon – Thomastown 220 kV line in at South Morang Terminal Station | $3.5M (Eastern Victoria Grid Reinforcement RIT-T,PSCR) | $0.035M | 50% | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab
Appendix A4.4 | Monitored | Murray River Corridor | Kerang - Bendigo 220 kV | Increased generation in regional Victoria. | 35.771⁰ S 143.934⁰ E | 36.784⁰ S 144.254⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Options Considered: - Replace the existing Kerang - Bendigo 220 kV line with a new double-circuit 220 kV circuit line and establish associated new terminal stations or existing station augmentations - Install an automatic load shedding control scheme to enable the use of five minute line rating | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Section 4.2.1 and Appendix A4.4 | Priority | Murray River Corridor | Red Cliffs - Wemen 220 kV | High Victorian demand post the commissioning of EnergyConnect and retirement of YWPS. | 34.292⁰ S 142.239⁰ E | 34.787⁰ S 142.524⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Options considered: - Build a second Red Cliffs – Wemen – Koorangie – Kerang 220 kV line by either building a new single-circuit or building a new double-circuit and retiring the existing line. - Install a Power Flow Controller (or similar device) on the Red Cliffs – Wemen – Koorangie – Kerang 220 kV line to divert flow away from the line at times of high demand. - Contracting BESS to charge or discharge, as required, to manage thermal loading on the Red Cliffs – Wemen – Kerang 220 kV line during peak loading periods. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab
Section 4.2.1 and Appendix A4.4 | Priority | Murray River Corridor | Wemen - Koorangie 220 kV | High Victorian demand post the commissioning of EnergyConnect and retirement of YWPS | 34.787⁰ S 142.524⁰ E | 35.730⁰ S 143.753⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab
Section 4.2.1 and Appendix A4.4 | Priority | Murray River Corridor | Koorangie - Kerang 220 kV | High Victorian demand post the commissioning of EnergyConnect and retirement of YWPS | 35.730⁰ S 143.753⁰ E | 35.771⁰ S 143.934⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  |  | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab
Appendix A4.5 | Monitored | South West Victoria Corridor | Moorabool - Heywood 500 kV | New generation connections along the Moorabool – Heywood – Alcoa Portland 500 kV line potentially introduce voltage unbalance along the line. The impact of voltage unbalance levels increases in proportion to power flow, new generation connection points, and output generated. | 38.037⁰ S 144.296⁰ E | 38.181⁰ S 141.639⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland. Install phase switched power flow controllers at Heywood or near Alcoa Portland. An SVC or a STATCOM. Additional transposition towers along the Moorabool – Heywood – Alcoa Portland 500 kV line. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Heywood - Portland 500 kV | New generation connections along the Moorabool – Heywood – Alcoa Portland 500 kV line potentially introduce voltage unbalance along the line. The impact of voltage unbalance levels increases in proportion to power flow, new generation connection points, and output generated. | 38.181⁰ S 141.639⁰ E | 38.387⁰ S 141.631⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Moorabool - Cressy 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 37.999⁰ S 143.752⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | A new Moorabool – Mortlake/Tarrone – Heywood 500 kV line. Line limiting plant upgrades. Install wind monitoring dynamic line rating scheme. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Cressy - Haunted Gully 500 kV | New generation | 37.999⁰ S 143.752⁰ E | 38.008⁰ S 143.313⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Haunted Gully -Mortlake 500 kV | New generation | 38.008⁰ S 143.313⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Mortlake - Tarrone 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.179⁰ S 142.181⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Cressy - Mortlake 500 kV | New generation | 37.999⁰ S 143.752⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | A new Moorabool – Mortlake/Tarrone – Heywood 500 kV line. Line limiting plant upgrades. Install wind monitoring dynamic line rating scheme. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Mortlake - Heywood 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.181⁰ S 141.639⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Tarrone - Heywood 500 kV | New generation | 38.179⁰ S 142.181⁰ E | 38.181⁰ S 141.639⁰ E | Note 5 | Same as Asset Rating | 500 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Ballarat - Berrybank 220 kV | Increased generation in regional Victoria | 37.567⁰ S 143.921⁰ E | 37.886⁰ S 143.453⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. Replace the existing Ballarat – Berrybank – Terang – Gnarwarre – Moorabool 220 kV line with a new double-circuit 220 kV circuit line | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Berrybank - Terang 220 kV | Increased generation in regional Victoria | 37.886⁰ S 143.453⁰ E | 38.233⁰ S 142.932⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Terang - Gnarwarre 220 kV | Increased generation in regional Victoria | 38.233⁰ S 142.932⁰ E | 38.147⁰ S 144.127⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Appendix A4.5 | Monitored | South West Victoria Corridor | Gnarwarre - Moorabool 220 kV | Increased generation in regional Victoria | 38.147⁰ S 144.127⁰ E | 38.037⁰ S 144.296⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Section 4.2.1 and Appendix A4.6 | Priority | Greater Mel & Geelong | Ringwood - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne. Reduced supply from Eastern Victoria and increased supply from Western Victoria. | 37.821⁰ S 145.216⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | The credible network option currently being assessed as part of East Metro RIT-T: - Bringing forward VNI West works to cut the Eildon – Thomastown 220 kV line into South Morang Terminal Station. - Install a new 500/220 kV transformer at Rowville (or Cranbourne) - Replacing equipment at metropolitan terminal stations that have fault level exceedances. | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | 50% | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Appendix A4.6 | Monitored | Greater Mel & Geelong | Templestowe - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne. Reduced supply from Eastern Victoria and increased supply from Western Victoria. | 37.748⁰ S 145.171⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | The credible network option currently being assessed as part of East Metro RIT-T: - Bringing forward VNI West works to cut the Eildon – Thomastown 220 kV line into South Morang Terminal Station. - Install a new 500/220 kV transformer at Rowville (or Cranbourne) - Replacing equipment at metropolitan terminal stations that have fault level exceedances. | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | 50% | Not available. | Not available. | Not available. |  |  |  | $35,780/MWh
Appendix A4.6 | Monitored | Greater Mel & Geelong | Rowville - Malvern 220 kV | Increased demand or additional loads connected to Malvern Terminal Station. | 37.929⁰ S 145.227⁰ E | 37.878⁰ S 145.084⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut-in Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | Rowville - Springvale 220 kV | Increased demand or additional loads connected to Springvale and Heatherton Terminal Station. | 37.929⁰ S 145.227⁰ E | 37.928⁰ S 145.146⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a third Rowville –Springvale circuit (underground cable). Connect a Cranbourne – Heatherton 220 kV double circuit overhead line. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | Springvale - Heatherton 220 kV |  | 37.928⁰ S 145.146⁰ E | 37.941⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 220 kV | [5 empty] | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | South Morang - Thomastown No. 1 and No.2 220 kV | Increased demand around the Melbourne Metropolitan area and/or increased export to New South Wales. Generation planting and retirements as per the 2024 ISP Step Change scenario. | 37.644⁰ S 145.078⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Increase the transfer capability by installing wind monitoring facilities on the South Morang to Thomastown line. Install an automatic load shedding control scheme to enable the use of five-minute line rating. Install a third 500/220 kV transformer at Rowville, plus any fault level mitigation works. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Section 4.2.1 and Appendix A4.6 | Priority | Greater Mel & Geelong | Moorabool - Geelong 220 kV | Large-scale new generation connected to western Victoria area, and congestion within western Victoria relieved to allow the new generation to be sent out of western Victoria. Generation planting and retirements as per the 2024 ISP Step Change scenario Increased maximum demand in Metro Melbourne | 38.037⁰ S 144.296⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR | The credible network option currently being assessed as part of West Metro RIT-T: - Deer Park cut in with Moorabool to Geelong uprate. - Cut Geelong – Keilor No.1 and No.3 220 kV lines into Deer Park and potentially operate the Deer Park – Keilor circuits as normally open. Under this arrangement Deer Park would be supplied from Geelong. - Perform works to increase line rating of existing Geelong – Moorabool 220 kV lines (replace limiting plant and install wind monitoring). | $73.6M (including additional works assessed as part of Western Metropolitan Melbourne Reinforcement RIT-T) | $0.736M | 50% | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Section 4.2.1 and Appendix A4.6 | Priority | Greater Mel & Geelong | Geelong - Keilor 220 kV | Increased generation from the southwest area and high demand in Melbourne metropolitan area | 38.083⁰ S 144.339⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR |  |  |  |  | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Section 4.2.1 and Appendix A4.6 | Priority | Greater Mel & Geelong | Keilor - Deer Park 220 kV | Demand growth in the western metropolitan area supplied from Deer Park terminal station | 37.738⁰ S 144.846⁰ E | 37.778⁰ S 144.735⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR |  |  |  |  | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Section 4.2.1 and Appendix A4.6 | Priority | Greater Mel & Geelong | Deer Park - Geelong 220 kV | Demand growth in the western metropolitan area supplied from Deer Park terminal station | 37.778⁰ S 144.735⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR | Refer Western Metropolitan Melbourne Reinforcement RIT-T,PSCR |  |  |  |  | Not available. | Not available. | Not available. | Refer Line Loadings Tab | Refer Line Ratings Tab |  | $35,780/MWh
Appendix A4.6 | Monitored | Greater Mel & Geelong | Altona - Keilor 220 kV | Increased maximum demand in Metropolitan Melbourne. | 37.839⁰S, 144.789⁰E | 37.826⁰S, 144.860⁰E | Note 5 | Same as Asset Rating | 220 kV |  |  | Western Metropolitan Grid Reinforcement RIT-T will provide a holistic solution to address limitations | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | Brooklyn - Keilor 220 kV | Increased maximum demand in Metropolitan Melbourne. | 37.826⁰S, 144.860⁰E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Western Metropolitan Grid Reinforcement RIT-T will provide a holistic solution to address limitations | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | Keilor - Thomastown No. 1 220 kV | Reduced supply from Eastern Victoria and increased supply from Western Victoria. | 37.738⁰ S 144.846⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Install an automatic load shedding control scheme to enable the use of five-minute line rating Install a third 500/220 kV transformer at Rowville, plus any fault level mitigation works. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.6 | Monitored | Greater Mel & Geelong | Sydenham - Keilor 500 kV | Increased generation in west and southwest Victoria supplying Keilor Terminal Station. | 37.676⁰ S 144.747⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Install a new single circuit Sydenham – Keilor 500 kV line with a rating of approximately 2,900 MVA at 35°C. Uprate line rating of the existing Sydenham – Keilor 500 kV line. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.7 | Monitored | Western Victoria Corridor | Red Cliffs - Kiamal 220 kV | Increased generation in Western Victoria and Murray River Corridor. | 34.292⁰ S 142.239⁰ E | 35.030⁰ S 142.294⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. Install a new double circuit Bulgana to Murra Warra 220kV line via a new terminal station at Horsham. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
Appendix A4.7 | Monitored | Western Victoria Corridor | Kiamal - Murra Warra 220 kV |  | 35.030⁰ S 142.294⁰ E | 36.433⁰ S 142.320⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Appendix A4.7 | Monitored | Western Victoria Corridor | Murra Warra - Horsham 220 kV |  | 36.433⁰ S 142.320⁰ E | 36.722⁰ S 142.248⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Appendix A4.7 | Monitored | Western Victoria Corridor | Horsham - Bulgana 220 kV |  | 36.722⁰ S 142.248⁰ E | 37.037⁰ S 142.984⁰ E | Note 5 | Same as Asset Rating | 220 kV | [7 empty] | Not available. | Not available.
Note 1: As those lines are associated with existing constraints, their maximum line loads are expected to be their ratings.
Note 2: The annual constraint duration values are the estimated next available year forecasts based on information from the corresponding RIT-Ts.
Note 3: The constraint duration on peak demand day is based on available estimated forecasts from the corresponding RIT-Ts or historical data if forecasts are unavailable.
Note 4: The investment option with possibly the lowest cost has been provided, as per Appendix A4 of the 2025 APR. All DSN augmentation costs are under review, given recent significant changes in material and labour costs.
Note 5: See asset ratings available on AEMO's website at http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings

## Summary Sgmt data-2021 unsorted (hidden)
VAPR Section Reference | Limitation Type | Victorian Region | Transmission Line ID | Constraint Primary Driver | Location of constraint (start) | Location of constraint (end) | Asset Rating (Load Shed @35°C) | Forecast Demand (note 1) | Voltage Level | Maximum load at risk per year | Energy at risk | Preferred investment - Description (note 4) | Preferred investment - Capital cost | Preferred investment - Annual operating cost | Preferred investment — Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MW) | Annual deferral value ($million) | Historic line load trace | Historic line rating | Annual economic cost of constraint | VCR ($/MWh) | Annual constraint duration (note 2) | Constraint duration on peak demand day (note 3)
Section 4.4 and Appendix A2.2 | Developing | Eastern Corridor | Hazelwood – Yallourn 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit line with one or two circuits strung, or rebuild existing double circuit line at a higher rating. | $31,500,000-$37,100,000 | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Hazelwood – Rowville 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 37.928⁰ S 145.226⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Hazelwood – Rowville 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Hazelwood – Rowville 220 kV line with one or two circuits strung post Yallourn power station retirement. | Not available. | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Rowville - Yallourn 220 kV | High generation output and high temperature | 37.928⁰ S 145.226⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Rowville-Yallourn 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Rowville-Yallourn 220 kV line with one or two circuits strung post Yallourn power station retirement.
Section 4.4 and Appendix A2.2 | Developing (Line outage), Monitored (no line outage) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Lack of outage window period due to constricted generation secure support across demand range post Yallourn Power Station retirement. | 38.273⁰ S 146.392⁰ E | 38.256⁰ S 146.573⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Construct a new single or double circuit Hazelwood-Loy Yang 500kV line with one or two circuits strung. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Heywood 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 |  | 500 kV |  |  | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland. | 15300000 | Not available. | ±50% | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Heywood - Portland 500 kV | New generation | 38.182⁰ S 141.638⁰ E | 38.387⁰ S 141.626⁰ E | Note 5 |  | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Mortlake 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Install a wind monitoring scheme. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Haunted Gully 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.007⁰ S 143.315⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Haunted Gully - Tarrone 500 kV | New generation | 38.007⁰ S 143.315⁰ E | 38.179⁰ S 142.181⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Mortlake - Heywood 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Tarrone - Heywood 500 kV | New generation | 38.179⁰ S 142.181⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Dederang - Mount Beauty 220 kV | Increased metro Melbourne demand, new generation and increased interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.743⁰ S 147.165⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme and up-rate the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82ºC. | 13300000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Mount Beauty - Eildon 220 kV | New generation and increased interconnector transfer | 36.743⁰ S 147.165⁰ E | 37.224⁰ S 145.921⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Mount Beauty and Eildon to 75ºC. Up-rate terminations to match line. | 114900000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Eildon - Thomastown 220 kV | Increased interconnector transfer | 37.224⁰ S 145.921⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Eildon and Thomstown to 75ºC. Up-rate terminations to match line. |  | Not available. | ±50% | Not available.
Appendix A2.3 | Monitored | Northern Corridor | Murray - Dederang 330 kV | High generation output or increased interconnector transfer | 36.226⁰ S 148.144⁰ E | 36.454⁰ S 146.992⁰ E | Note 5 | Same as Asset Rating | 330 kV |  |  | Install a new 1,060 MVA 330 kV line to Dederang (or a newly established station nearby)- a third line from Murray, or a second line from Jindera. | Not available. | Not available. |  | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Ringwood - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne and/or Latrobe Valley operated in radial configuration after Yallourn Power Station retirement. | 37.821⁰ S 145.216⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut in Rowville – Ringwood – Thomastown 220 kV at Templestowe and Rowville – Templestowe – Thomastown 220 kV at Ringwood to form the Rowville – Ringwood – Templestowe – Thomastown No. 1 and No. 2 circuits. | $15,100,000 plus any fault mitigation costs. | Not available. | ±50% | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Templestowe - Thomastown 220 kV |  | 37.749⁰ S 145.171⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Malvern 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.878⁰ S 145.084⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut-in Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits. | 11800000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Springvale 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.928⁰ S 145.146⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a Cranbourne – Heatherton 220 kV double circuit overhead line. | 38000000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Springvale - Heatherton 220 kV | Increased demand | 37.928⁰ S 145.146⁰ E | 37.941⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | South Morang - Thomastown 220 kV | Increased demand around the Melbourne Metropolitan area and/or increased export to New South Wales and/or Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.644⁰ S 145.078⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Increase the transfer capability by installing wind monitoring facilities on the South Morang to Thomastown line. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Moorabool - Geelong 220 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a new double circuit Moorabool – Geelong 220kV line with a rating of approximately 800 MVA per circuit at 35ºC. | $42,700,00 | Not available. | ±50% | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Geelong - Keilor 220 kV | New generation | 38.083⁰ S 144.339⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Replace the existing Geelong-Keilor 220 kV double circuit line (circuits 1 and 3) with a new double circuit line, each circuit rated at 800 MVA at 35ºC. | $190,500,00
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Deer Park 220 kV | Increased demand | 37.738⁰ S 144.846⁰ E | 37.778⁰ S 144.735⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a load shedding control scheme. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Deer Park - Geelong 220 kV | Increased demand | 37.778⁰ S 144.735⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Thomastown No. 1 220 kV | Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.738⁰ S 144.846⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. |  | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Sydenham - Keilor 500 kV | New generation | 37.676⁰ S 144.747⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Increase station plant ratings to remove station thermal constraints on line. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Red Cliffs - Kiamal 220 kV | New and retired generation | 34.275⁰ S 142.2⁰ E | 35.031⁰ S 142.293⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not Available | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Kiamal - Murra Warra 220 kV | New and retired generation | 35.031⁰ S 142.293⁰ E | 36.433⁰ S 142.318⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Murra Warra - Horsham 220 kV | New and retired generation | 36.433⁰ S 142.318⁰ E | 36.731⁰ S 142.246⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Horsham - Bulgana 220 kV | New and retired generation | 36.731⁰ S 142.246⁰ E | 37.037⁰ S 142.984⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Red Cliffs - Wemen 220 kV | New and retired generation, and high temperature | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Wemen - Kerang 220 kV | New and retired generation, and high temperature | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Kerang - Bendigo 220 kV | New and retired generation | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Red Cliffs - Wemen 220 kV | Increased demand | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Appendix A2.4 | Monitored | Murray River REZ | Wemen - Kerang 220 kV | Increased demand | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Kerang - Bendigo 220 kV | Increased demand | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Ballarat - Terang 220 kV | New generation | 37.567⁰ S 143.921⁰ E | 38.256⁰ S 142.925⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Terang - Moorabool 220 kV | New generation | 38.256⁰ S 142.925⁰ E | 38.037⁰ S 144.296⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Dederang - Glenrowan 220 kV | New generation, increased demand and interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.494⁰ S 146.075⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding and generation runback control scheme to enable the use of five minute line rating. | 1500000 | Not available. | ±50% | Not available.
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Glenrowan - Shepparton 220 kV | New generation, increased demand and interconnector transfer | 36.494⁰ S 146.075⁰ E | 36.353⁰ S 145.365⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Shepparton - Bendigo 220 kV | New generation, increased demand and interconnector transfer | 36.353⁰ S 145.365⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Note 1: As those lines are associated with existing constraints, their maximum line loads are expected to be their ratings.
Note 2: The annual constraint duration values are the estimated next available year forecasts based on information from the corresponding RIT-Ts. For West VIC RIT-T constraints, annual constraint duration is based on 2021 forecasts.
Note 3: The constraint duration on peak demand day is based on available estimated forecasts from the corresponding RIT-Ts or historical data if forecasts are unavailable.
Note 4: The investment option with the lowest cost has been provided, as per Appendix A1 of the 2021 VAPR. This investment is indicative only, and the preferred option will be determined as per the required RIT-T assessment.
Note 5: See asset ratings available on AEMO's website at http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings

## Annual Cost of Constraint
Values shown are the respective annualised cost of each constraint in $million.
| Hazelwood - Yallourn 220 kV | Rowville - Yallourn 220 kV | Eildon - Thomastown 220 kV | Red Cliffs - Wemen - Koorangie - Kerang 220 kV | Ringwood - Thomastown 220 kV | Moorabool - Geelong 220 kV | Geelong - Keilor 220 kV | Keilor - Deer Park - Geelong 220 kV | Rowville A1 500/220 kV Transformer | Keilor A2 & A4 500/220 kV Transformers
2025-2026 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2026-2027 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2027-2028 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2028-2029 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2029-2030 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2030-2031 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2031-2032 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2032-2033 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2033-2034 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
2034-2035 | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available. | Not available.
`

## Asset Rating
Ratings shown are the respective 35°C load shed ratings (MVA) for each line (note 1), as available from:
https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings
| Hazelwood - Yallourn 220 kV |  | Rowville - Yallourn 220 kV |  |  |  | Eildon - Thomastown 220 kV | Red Cliffs - Wemen - Koorangie - Kerang 220 kV |  |  | Ringwood - Thomastown 220 kV | Moorabool - Geelong 220 kV |  | Geelong - Keilor 220 kV |  | Keilor - Deer Park - Geelong 220 kV |  | Rowville 500/220 kV Transformer | Keilor A2 & A4 500/220 kV Transformers
| Hazelwood - Yallourn 1 220 kV line | Hazelwood - Yallourn 2 220 kV line | Rowville - Yallourn 5 220 kV line | Rowville - Yallourn 6 220 kV line | Rowville - Yallourn 7 220 kV line | Rowville - Yallourn 8 220 kV line | Eildon - Thomastown 220 kV line | Red Cliffs - Wemen 220 kV line | Koorangie - Wemen 220 kV line | Kerang - Koorangie 220 kV line | Ringwood - Thomastown 220 kV line | Geelong - Moorabool 1 220 kV line | Geelong - Moorabool 2 220 kV line | Geelong - Keilor 1 220 kV line | Geelong - Keilor 3 220 kV line | Keilor - Deer Park 220 kV line | Deer Park - Geelong 220 kV line | Rowville A1 500/220 kV transformer | Keilor A2 500/220 kV transformer | Keilor A4 500/220 kV Transformer
2025-2026 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2026-2027 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2027-2028 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2028-2029 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2029-2030 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2030-2031 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2031-2032 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2032-2033 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2033-2034 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
2034-2035 | 413 | 413 | 305 | 305 | 305 | 305 | 541 | 267 | 267 | 267 | 705 | 800 | 827 | 271 | 271 | 271 | 271 | 1000 | 750 | 750
Note 1: Dynamic ratings are applied to the Victorian Transmission lines and therefore the actual line ratings are dependent on weather conditions, mainly ambient temperature in real time.
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Should we include ROTS and KTS transformers here?