## Summary Sgmt data-2021 unsorted (hidden)
VAPR Section Reference | Limitation Type | Victorian Region | Transmission Line ID | Constraint Primary Driver | Location of constraint (start) | Location of constraint (end) | Asset Rating (Load Shed @35°C) | Forecast Demand (note 1) | Voltage Level | Maximum load at risk per year | Energy at risk | Preferred investment - Description (note 4) | Preferred investment - Capital cost | Preferred investment - Annual operating cost | Preferred investment — Cost accuracy | Preferred investment - Proposed timing | Demand reduction required to defer investment by 1 year (MW) | Annual deferral value ($million) | Historic line load trace | Historic line rating | Annual economic cost of constraint | VCR ($/MWh) | Annual constraint duration (note 2) | Constraint duration on peak demand day (note 3)
Section 4.4 and Appendix A2.2 | Developing | Eastern Corridor | Hazelwood – Yallourn 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Construct a new single or double circuit line with one or two circuits strung, or rebuild existing double circuit line at a higher rating. | $31,500,000-$37,100,000 | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Hazelwood – Rowville 220 kV | High generation output and high temperature | 38.273⁰ S 146.392⁰ E | 37.928⁰ S 145.226⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Hazelwood – Rowville 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Hazelwood – Rowville 220 kV line with one or two circuits strung post Yallourn power station retirement. | Not available. | Not available. |  | Not available.
Appendix A2.2 | Monitored | Eastern Corridor | Rowville - Yallourn 220 kV | High generation output and high temperature | 37.928⁰ S 145.226⁰ E | 38.177⁰ S 146.344⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Upgrade Rowville-Yallourn 220 kV line prior to Yallourn power station retirement, or construct a new single or double circuit Rowville-Yallourn 220 kV line with one or two circuits strung post Yallourn power station retirement.
Section 4.4 and Appendix A2.2 | Developing (Line outage), Monitored (no line outage) | Eastern Corridor | Hazelwood – Loy Yang 500 kV | Lack of outage window period due to constricted generation secure support across demand range post Yallourn Power Station retirement. | 38.273⁰ S 146.392⁰ E | 38.256⁰ S 146.573⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Construct a new single or double circuit Hazelwood-Loy Yang 500kV line with one or two circuits strung. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Heywood 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 |  | 500 kV |  |  | A switched capacitor with individual phase switching at Heywood or near Alcoa Portland. | 15300000 | Not available. | ±50% | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Heywood - Portland 500 kV | New generation | 38.182⁰ S 141.638⁰ E | 38.387⁰ S 141.626⁰ E | Note 5 |  | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Mortlake 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.062⁰ S 142.67⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Install a wind monitoring scheme. | Not available. | Not available. |  | Not available.
Appendix A2.5 | Monitored | South West Victoria REZ | Moorabool - Haunted Gully 500 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.007⁰ S 143.315⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Haunted Gully - Tarrone 500 kV | New generation | 38.007⁰ S 143.315⁰ E | 38.179⁰ S 142.181⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Mortlake - Heywood 500 kV | New generation | 38.062⁰ S 142.67⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Appendix A2.5 | Monitored | South West Victoria REZ | Tarrone - Heywood 500 kV | New generation | 38.179⁰ S 142.181⁰ E | 38.182⁰ S 141.638⁰ E | Note 5 | Same as Asset Rating | 500 kV
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Dederang - Mount Beauty 220 kV | Increased metro Melbourne demand, new generation and increased interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.743⁰ S 147.165⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme and up-rate the conductor temperature of both 220 kV circuits between Dederang and Mount Beauty to 82ºC. | 13300000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Mount Beauty - Eildon 220 kV | New generation and increased interconnector transfer | 36.743⁰ S 147.165⁰ E | 37.224⁰ S 145.921⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Mount Beauty and Eildon to 75ºC. Up-rate terminations to match line. | 114900000 | Not available. | ±50% | Not available.
Section 6.3.3 and Appendix A2.3 | Monitored | Ovens Murray REZ | Eildon - Thomastown 220 kV | Increased interconnector transfer | 37.224⁰ S 145.921⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. Up-rate the conductor temperature of both 220 kV circuits between Eildon and Thomstown to 75ºC. Up-rate terminations to match line. |  | Not available. | ±50% | Not available.
Appendix A2.3 | Monitored | Northern Corridor | Murray - Dederang 330 kV | High generation output or increased interconnector transfer | 36.226⁰ S 148.144⁰ E | 36.454⁰ S 146.992⁰ E | Note 5 | Same as Asset Rating | 330 kV |  |  | Install a new 1,060 MVA 330 kV line to Dederang (or a newly established station nearby)- a third line from Murray, or a second line from Jindera. | Not available. | Not available. |  | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Ringwood - Thomastown 220 kV | Increased demand in Eastern Metropolitan Melbourne and/or Latrobe Valley operated in radial configuration after Yallourn Power Station retirement. | 37.821⁰ S 145.216⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut in Rowville – Ringwood – Thomastown 220 kV at Templestowe and Rowville – Templestowe – Thomastown 220 kV at Ringwood to form the Rowville – Ringwood – Templestowe – Thomastown No. 1 and No. 2 circuits. | $15,100,000 plus any fault mitigation costs. | Not available. | ±50% | Not available.
Section 4.6.2 and Appendix A2.6 | Monitored | Greater Mel & Geelong | Templestowe - Thomastown 220 kV |  | 37.749⁰ S 145.171⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Malvern 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.878⁰ S 145.084⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Cut-in Rowville–Richmond 220 kV No.1 and No.4 circuits at Malvern Terminal Station to form the Rowville–Malvern–Richmond No.3 and No.4 circuits. | 11800000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Rowville - Springvale 220 kV | Increased demand | 37.928⁰ S 145.226⁰ E | 37.928⁰ S 145.146⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a Cranbourne – Heatherton 220 kV double circuit overhead line. | 38000000 | Not available. | ±50% | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Springvale - Heatherton 220 kV | Increased demand | 37.928⁰ S 145.146⁰ E | 37.941⁰ S 145.078⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | South Morang - Thomastown 220 kV | Increased demand around the Melbourne Metropolitan area and/or increased export to New South Wales and/or Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.644⁰ S 145.078⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Increase the transfer capability by installing wind monitoring facilities on the South Morang to Thomastown line. | Not available. | Not available. |  | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Moorabool - Geelong 220 kV | New generation | 38.037⁰ S 144.296⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Connect a new double circuit Moorabool – Geelong 220kV line with a rating of approximately 800 MVA per circuit at 35ºC. | $42,700,00 | Not available. | ±50% | Not available.
Section 4.4 and Appendix A2.6 | Developing | Greater Mel & Geelong | Geelong - Keilor 220 kV | New generation | 38.083⁰ S 144.339⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Replace the existing Geelong-Keilor 220 kV double circuit line (circuits 1 and 3) with a new double circuit line, each circuit rated at 800 MVA at 35ºC. | $190,500,00
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Deer Park 220 kV | Increased demand | 37.738⁰ S 144.846⁰ E | 37.778⁰ S 144.735⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a load shedding control scheme. | Not available. | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Deer Park - Geelong 220 kV | Increased demand | 37.778⁰ S 144.735⁰ E | 38.083⁰ S 144.339⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.6 | Monitored | Greater Mel & Geelong | Keilor - Thomastown No. 1 220 kV | Latrobe Valley operated in a radial configuration after Yallourn Power Station retirement. | 37.738⁰ S 144.846⁰ E | 37.693⁰ S 145.01⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install a wind monitoring scheme. |  | Not available. |  | Not available.
Appendix A2.6 | Monitored | Greater Mel & Geelong | Sydenham - Keilor 500 kV | New generation | 37.676⁰ S 144.747⁰ E | 37.738⁰ S 144.846⁰ E | Note 5 | Same as Asset Rating | 500 kV |  |  | Increase station plant ratings to remove station thermal constraints on line. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Red Cliffs - Kiamal 220 kV | New and retired generation | 34.275⁰ S 142.2⁰ E | 35.031⁰ S 142.293⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not Available | Not available. |  | Not available.
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Kiamal - Murra Warra 220 kV | New and retired generation | 35.031⁰ S 142.293⁰ E | 36.433⁰ S 142.318⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Murra Warra - Horsham 220 kV | New and retired generation | 36.433⁰ S 142.318⁰ E | 36.731⁰ S 142.246⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.4.3 and Appendix A2.7 | Priority | Western Victoria REZ | Horsham - Bulgana 220 kV | New and retired generation | 36.731⁰ S 142.246⁰ E | 37.037⁰ S 142.984⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Red Cliffs - Wemen 220 kV | New and retired generation, and high temperature | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Wemen - Kerang 220 kV | New and retired generation, and high temperature | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.4 | Priority | Murray River REZ | Kerang - Bendigo 220 kV | New and retired generation | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Red Cliffs - Wemen 220 kV | Increased demand | 34.275⁰ S 142.2⁰ E | 34.791⁰ S 142.522⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Appendix A2.4 | Monitored | Murray River REZ | Wemen - Kerang 220 kV | Increased demand | 34.791⁰ S 142.522⁰ E | 35.782⁰ S 143.945⁰ E | Note 5 | Same as Asset Rating | 220 kV
Appendix A2.4 | Monitored | Murray River REZ | Kerang - Bendigo 220 kV | Increased demand | 35.782⁰ S 143.945⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Ballarat - Terang 220 kV | New generation | 37.567⁰ S 143.921⁰ E | 38.256⁰ S 142.925⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic generation runback control scheme to enable the use of five minute line rating. | Not available. | Not available. |  | Not available.
Sections 4.3 and 6.3.3 and Appendix A2.5 | Priority | South West Victoria REZ | Terang - Moorabool 220 kV | New generation | 38.256⁰ S 142.925⁰ E | 38.037⁰ S 144.296⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Dederang - Glenrowan 220 kV | New generation, increased demand and interconnector transfer | 36.454⁰ S 146.992⁰ E | 36.494⁰ S 146.075⁰ E | Note 5 | Same as Asset Rating | 220 kV |  |  | Install an automatic load shedding and generation runback control scheme to enable the use of five minute line rating. | 1500000 | Not available. | ±50% | Not available.
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Glenrowan - Shepparton 220 kV | New generation, increased demand and interconnector transfer | 36.494⁰ S 146.075⁰ E | 36.353⁰ S 145.365⁰ E | Note 5 | Same as Asset Rating | 220 kV
Sections 4.4 and 6.3.3 and Appendix A2.1 | Developing | Central North REZ | Shepparton - Bendigo 220 kV | New generation, increased demand and interconnector transfer | 36.353⁰ S 145.365⁰ E | 36.796⁰ S 144.252⁰ E | Note 5 | Same as Asset Rating | 220 kV
Note 1: As those lines are associated with existing constraints, their maximum line loads are expected to be their ratings.
Note 2: The annual constraint duration values are the estimated next available year forecasts based on information from the corresponding RIT-Ts. For West VIC RIT-T constraints, annual constraint duration is based on 2021 forecasts.
Note 3: The constraint duration on peak demand day is based on available estimated forecasts from the corresponding RIT-Ts or historical data if forecasts are unavailable.
Note 4: The investment option with the lowest cost has been provided, as per Appendix A1 of the 2021 VAPR. This investment is indicative only, and the preferred option will be determined as per the required RIT-T assessment.
Note 5: See asset ratings available on AEMO's website at http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Network-Data/Transmission-Equipment-Ratings