## Disclaimer
Disclaimer
This workbook may be of assistance to you but VicGrid and its officers and employees do not guarantee it is
without flaw or appropriate for your particular purposes and, therefore, disclaims all liability for any error, loss or
other consequence arising from your reliance on any information in it.
VicGrid has made reasonable efforts to ensure the quality of the information in this workbook, but cannot guarantee
that information, forecasts, and assumptions are accurate, complete or appropriate for your circumstances.
Modelling work performed as part of preparing this workbook inherently requires assumptions about future
behaviours and market interactions that may result in forecasts that deviate from future conditions. There will
usually be differences between estimated and actual results, because events and circumstances frequently do not
occur as expected, and those differences could be material.
This workbook does not include all information that an investor, participant, or potential participant in the National
Electricity Market might require and does not amount to a recommendation of any investment. Anyone proposing to
use the information in this workbook (which includes information and forecasts from third parties) should
independently verify its accuracy, completeness and suitability for purpose and obtain independent and specific
advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, VicGrid and its officers, employees and consultants involved
in the preparation of this workbook:
· make no express or implied representation or warranty as to the currency, accuracy, reliability or
completeness of the information in this workbook; and
· are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information
or other matters contained in or derived from this workbook, or any omissions from it, or in respect of a
person’s use of the information in this workbook.

## Introduction
In December 2018, AER made a final determination on a new Transmission Annual Planning Report (TAPR) Guideline, requiring TNSPs to publish specified information on emerging transmission line and terminal station limitations.
The "Summary of Transmission connection point (TCP) data" spreadsheet provides information on a selected set of transmission terminal stations associated with Declared Shared Network(DSN) transformer emerging limitations and connection asset limitations.
The DSN transformer priority limitations were selected based on VicGrid’s VAPR, 2025 VTP and RIT-T reports, and the connection asset limitations were selected based on the 2025 Transmission Connection Planning report (TCPR), produced jointly by the Victorian Electricity Distribution Businesses.
As VicGrid's projects are still works in progress, the information provided is subject to change.
The general criteria for selecting the existing assets to be included in the data reporting are:
• For DSN assets, they are associated with both load and generation driven priority or monitored limitations for which VicGrid has yet to finalise the preferred option to address.
• For connection assets , their augmentations are required in the near future according to the 2025 TCPR.
For connection assets, the information is based on that available in the 2025 TCPR and supplemented by RIT-T documentation. VicGrid has noted that some Victorian DNSPs may use their own connection point demand forecast, which is different from VicGrid’s connection point demand forecast
In addition to the information on priority limitations specified in the TAPR guideline, The "Summary of TCP data sheet" also includes information related to terminal stations with monitored limitations, and other terminal stations in Victoria.
The information on monitored limitations includes:
• Constrained connection point ID
• Constraint primary driver
• Constraint investment type
• Constrained connection point location
• Voltage level
• Preferred investment— Description
• Preferred investment — Capital cost (if available)
• Preferred investment— Cost accuracy (if available)
• Maximum fault level (3 phase or single phase)
The information on other terminal stations not associated with any limitation includes terminal station location, voltage level and maximum fault level at the high voltage side.

## Summary of TCP data 2021 (hidden)
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melourne & Geelong | Emerging | Altona West terminal station | Customer load at risk (market benefit) | Augmentation | 37.839oS, 144.789oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast spreadsheet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits | $18M | Unavailable from TCPR | Unavailable from TCPR | 2026 | 9 MW | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 158 MW (summer) | Unavailable from TCPR | Unavailable from TCPR | 19kA (66kV) | $1.79M in 2029 | $34,740/MWh | 51.6 MWh in 2029 | 51.5256
| Emerging | Cranbourne terminal station | Customer load at risk (market benefit) | Augmentation | 38.085oS, 145.265oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 4th 150MVA transformer | $26M | Unavailable from TCPR | Unavailable from TCPR | 2023 | 7MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 359MVA | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $2.46M in 2026 | $34,778/MWh | 70.8MWh in 2026 | 51.581
| Emerging | Deer Park terminal station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 3rd 225MVA transformer, initially "spare", not terminated. | $4M | Unavailable from TCPR | [9 empty] | 11kA (66kV) | $0.45M in 2026 | $38,272/MWh | 11.8MWh in 2026
| Monitored | South Morang terminal station | Increased demand in Metropolitan Melbourne and/or increased import from NSW. | Augmentation | 37.644⁰ S 145.078⁰ E | [7 empty] | 330/220kV |  |  | Replace the existing transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $44M |  | not available | 2024 | Not applicable | [6 empty] | 25kA (330kV)
| Developing | Cranbourne terminal station | Increased demand around the Eastern Melbourne Metropolitan area. | Augmentation | 38.085oS, 145.265oE | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $72.5M |  | 50% | [8 empty] | 17kA (500kV)
| Developing | Rowville terminal station | Increased demand in Eastern Metropolitan Melbourne. | Augmentation | 37.928⁰ S 145.226⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity at Cranbourne terminal station. | $72.5M |  | 50% | [8 empty] | 21kA (500kV)
Murray River REZ | Emerging | Wemen terminal station | Posible increased generation embedded inte distribution network. | Augmentation | 34.791⁰ S 142.522⁰ E | [7 empty] | 220kV |  |  | Install additional transformation capacity at Wemen terminal station. | Unavailable from TCPR | [10 empty] | 5kA
South - West Victoria REZ | Developing | Moorabool terminal station | Large-scale new generation in western Victoria area | Augmentation | 38.037⁰ S 144.296⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $102M |  | 50% | [8 empty] | 17kA (500kV)
Ovens Murray REZ | Developing | Dederang terminal station | High imports from NSW and Murray generation (with the DBUSS transformer control scheme being active). | Augmentation | 36.454⁰ S 146.992⁰ E | [7 empty] | 330/220kV |  |  | Install additional transformation capacity | Unavailable |  | 50% | [8 empty] | 18kA (330kV)
Eastern Corridor |  | Hazelwood terminal station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 27kA
|  | Hazelwood power station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 41kA
|  | Jeeralang terminal station |  |  | 38.275⁰ S 146.425⁰ E | [7 empty] | 220kV | [14 empty] | 33kA
|  | Loy Yang power staton |  |  | 38.254⁰ S 146.576⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Morwell terminal station |  |  | 38.259⁰ S 146.421⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
|  | Yallourn terminal station |  |  | 38.177⁰ S 146.344⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
Ovens Murray REZ |  | Wodonga terminal station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 10kA
|  | Mt Beauty terminal station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Eildon terminal station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Dartmouth terminal station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Mckay Creek terminal station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | West Kiewa terminal station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Bogong terminal station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | East Rowville terminal station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 220kV | [14 empty] | 32kA
|  | Tyabb terminal station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | Western Port terminal station |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Malvern terminal station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Springvale terminal station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Heatherton terminal station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Ringwood terminal station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Templestowe terminal station |  |  | 37.749⁰ S 145.171⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Thomastown terminal station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 220kV | [14 empty] | 29kA
|  | Richmond terminal station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
|  | Brunswick terminal station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Keilor terminal station |  |  | 37.738⁰ S 144.846⁰ E | [7 empty] | 500kV | [14 empty] | 30kA
|  | West Melbourne terminal station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Fishermans Bend terminal station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Brooklyn terminal station |  |  | 37.826⁰ S 144.86⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Newport terminal station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Laverton North terminal station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Geelong terminal station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
Central North REZ |  | Fosterville terminal station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Glenrowan terminal station |  |  | 36.494⁰ S 146.075⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Shepparton terminal station |  |  | 36.353⁰ S 145.365⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
Murray River REZ |  | Bendigo terminal station |  |  | 36.796⁰ S 144.252⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Kerang terminal station |  |  | 35.782⁰ S 143.945⁰ E | [7 empty] | 220kV | [14 empty] | 4kA
|  | Kiamal terminal station |  |  | 35.027⁰ S 142.299⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Red Cliffs terminal station |  |  | 34.275⁰ S 142.2⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
South West Victoria REZ |  | Heywood terminal station |  |  | 38.182⁰ S 141.638⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Berrybank substation |  |  | 37.900⁰ S 143.438⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Blue Gum substation |  |  | 38.067⁰ S 142.674⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Haunted Gully terminal station |  |  | 38.006⁰ S 143.317⁰ E | [7 empty] | 500kV | [14 empty] | 13kA
|  | Mortlake terminal station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Portland substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Tarrone terminal station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 8kA
|  | Terang terminal station |  |  | 38.256⁰ S 142.925⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
Western Victoria REZ |  | Ararat terminal station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Ballarat terminal station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Bulgana terminal station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Crowlands terminal station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Elaine terminal station |  |  | 37.731⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Horsham terminal station |  |  | 36.731⁰ S 142.246⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Murra Warra terminal station |  |  | 36.455⁰ S 142.321⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Waubra terminal station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
South Morang project annual deferral value is present value of a one year deferment of project cost, using 6% pa discount rate.
Altona West, Cranbourne, and Deer Park Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
[13 empty] | 50pcl | 10pcl | $M
[9 empty] | $M pa | $M capex |  | VCR | MWh | MWh |  | MWh
[8 empty] | ATS W | 1.33 | 18 | 0.073889 | 34740 | 43.07 | 71.44 | 1.7919 | 51.581 | 1.7919
[8 empty] | CBTS | 1.9 | 26 | 0.073077 | 34778 | 21 | 187 | 2.4623 | 70.8 | 2.4623
[8 empty] | DPTS | 0.3 | 4.0826 | 0.073483 | 38272 | 5.32 | 26.78 | 0.45 | 11.758 | 0.45

## Summary of TCP data
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melbourne & Geelong | Priority | Altona/Brooklyn Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.826⁰S, 144.860⁰E | 341 GWh in 2024 (refer PSCR for details) | 325 GWh in 2024 (refer PSCR for details) | 1522 GWh in 2024 (refer PSCR for details) | See "Altona_Brooklyn MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Refer Altona-Brooklyn Terminal Station Capacity Constraint RIT-T, PSCR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits at ATS or BLTS | $35M | $0.35M | +/- 30% (PSCR) | 2028 | 91 MVA (50th percentile) | Unavailable from TCPR | 13 MVA in 2025 (PSCR) | Unavailable from TCPR | 340 MVA (summer N-1 import) | Capacity limited by ATS-BLTS transformers. | Unavailable from TCPR | 21kA (66kV) | $23.7M in 2028. (TCPR) | $36,588/MWh (TCPR) | 646 MWh in 2028. (TCPR)
| Monitored | Altona West Terminal Station (Altona Bus 3&4) | Customer load at risk (market benefit) | Augmentation | 37.839⁰S, 144.789⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity (fourth transformer) and reconfigure 66 kV exits at ATS. | $35M | $0.35M | Unavailable from TCPR | 2029 | 76.4 MVA (50th percentile) | Unavailable from TCPR | 7.5 MVA (in summer 2025/26) | Unavailable from TCPR | 177 MVA until Q4 2026, then 354 MVA (summer N-1 import) | Capacity limited by ATS West transformers. | Unavailable from TCPR | 19kA (66kV) | $0.54M in 2035 (TCPR assumes 3rd transformer is installed) | $41,573/MWh | 13 MWh in 2035 (TCPR assumes 3rd transformer is installed)
| Priority | Cranbourne Terminal Station | Customer load at risk (market benefit) | Augmentation | 38.085⁰S, 145.265⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Refer Maintaining supply reliability in the Cranbourne supply area RIT-T, PACR | Unavailable from TCPR | Install a fourth transformer and associated work. | $63M (2025 AusNet & United Energy RIT-T, PACR) | $0.6M (2025 AusNet & United Energy RIT-T, PACR) | +/- 30% (PACR) | 2026/27 | 27 MVA (50th percentile) | Unavailable from TCPR | Refer Maintaining supply reliability in the Cranbourne supply area RIT-T, PACR | Unavailable from TCPR | 360MVA (summer N-1 import) with 3 transformers | Capacity limited by Cranbourne supply transformers | Unavailable from TCPR | 28kA (66kV) | $0.07M in 2026/27 (TCPR assumes 4 transformer is in service) | $41,612 /MWh | 1.6 MWh in 2026/27 (TCPR assumes 4 transformer is in service)
| Priority | Deer Park Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Refer Emerging Load Constraint: Deer Park Terminal Station RIT-T, PACR | Unavailable from TCPR | Install a third transformer and GTS-KTS lines cut into DPTS (PACR) | Total cost $86M Transformer cost $20M (DPTS RIT-T, PACR) | $0.43M (0.5% of Total capital cost) (DPTS RIT-T, PACR) | +/- 20% (PACR) | 2027 (PACR) | 98.2 MVA (50th percentile) | Unavailable from TCPR | 33.6 MVA (PACR) in summer 2025/26 | Unavailable from TCPR | 280 MVA (summer N-1 import) (PACR) | GTS-DPTS-KTS line and DPTS transformers | Unavailable from TCPR | 13kA (66kV) | $12.5M in 2027 (PACR) | $39,855/MWh (PACR) | 313.6 MWh in 2027
| Priority | Keilor Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.738⁰ S 144.846⁰ E | 832 GWh in 2024 (refer PADR for details) | 167 GWh in 2024 (refer PADR for details) | 693 GWh in 2024 (refer PADR for details) | See "Keilor MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Refer Keilor Terminal Station Capacity Constraint RIT-T, PADR | Unavailable from TCPR | Upgrade all three transformers at KTS B(1,2,5), install additional transformation capacity at KTS B(3,4) and transfer 66 kV exits from KTS B(1,2,5) to KTS B(3,4) group. | $91M | $0.9M | +/- 30% (PADR) | 2028/2029 | 115.4 MVA (50th percentile) | Unavailable from TCPR | 20 MVA KTS (B1,2,5) 15 MVA KTS (B3,4) (PADR) | Unavailable from TCPR | 370 MVA (B1,2,5) 341 MVA (B3,4) (summer N-1 import) | Capacity limited by KTS supply transformers. | Unavailable from TCPR | 23kA (66kV) B1 16kA (66kV) B3 | $33.47M (B1,2,5) in 2030 $25.53M (B3,4) in 2029 (TCPR) | $39,071/MWh (B1,2,5) $$44,243/MWh (B3,4) (TCPR) | 856.6 MWh (B1,2,5) in 2030 577 MWh (B3,4) in 2029 (TCPR)
| Priority | South Morang Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.644⁰ S 145.078⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "South Morang MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Refer South Morang Supply Area RIT-T, PADR | Unavailable from TCPR | Install a third 225 MVA 220/66kV transformer (PSCR) | $48.63M (PADR) | $0.5M (PADR) | +/- 30% (PADR) | 2028/2029 | 29 MVA (50th percentile) | Unavailable from TCPR | 0 MVA | Unavailable from TCPR | 259 MVA (summer N-1 import) | Capacity limited by SMTS supply transformers. | Unavailable from TCPR | 21kA (66kV) | $13.8M in 2026/27 (TCPR) | $40,730/MWh (TCPR) | 337 MWh in 2026/27 (assuming Somerton PS is unavailable) (TCPR)
| Monitored | Thomastown Terminal Station (B3,4) | Customer load at risk (market benefit) | Augmentation | 37.693⁰ S 145.01⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Thomastown MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install two new 150 MVA 220/66 kV transformers | $70M ($35M each) | $0.7M | Unavailable from TCPR | Between 2032-2033 | 53 MVA (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 319 MVA (summer N-1 import) | Capacity limited by TTS supply transformers. | Unavailable from TCPR | 23kA (66kV) | $2.37M in 2032 (TCPR) | $39,791.6/MWh (TCPR) | 59.6 MWh in 2032 (TCPR)
| Priority (VTP actioned) | Keilor Terminal Station (500/220 kV transformers) | Increased maximum demand in Metropolitan Melbourne, which is further exacerbated by retirement of YWPS. | Augmentation | 37.738⁰ S 144.846⁰ E | Unavailable | Unavailable | Unavailable |  |  |  |  | 500/220kV |  | N/A | VTP Projects 1.5, replace the existing A2, A3, A4 500/220 kV transformers at Keilor with upgraded units rated at 1000 MVA. The installation of a fourth 1000 MVA, 500/220 kV transformer at Keilor Terminal Station also represents a potential solution. | Refer 2025 Victoria Transmission Plan |  |  | Refer 2025 Victoria Transmission Plan |  |  |  |  | N/A | KTS 500/220kV transformers. |  | 24kA (500kV) 33kA (220kV)
| Priority (VTP actioned) | Rowville Terminal Station ((500/220 kV A1 transformer) | Increased demand in Metropolitan Melbourne area, which is further exacerbated by retirement of YWPS. | Augmentation | 37.929⁰ S 145.227⁰ E | Unavailable | Unavailable | Unavailable |  |  |  |  | 500/220kV |  | N/A | VTP Project 2.2, Install a second 500/220 kV transformer at Cranbourne and tie in the existing Hazelwood to Rowville 500 kV (No.3) circuit at Cranbourne, along with additional work of transferring the Rowville No. 2 500/220 kV transformer to the Rowville No. 3-4 220 kV Bus Group in parallel with the Rowville No. 1 500/220 kV transformer. | Refer 2025 Victoria Transmission Plan |  |  | Refer 2025 Victoria Transmission Plan |  |  |  |  | N/A | Capacity limited by ROTS 500/220kV transformers. |  | 23kA (500kV) 37kA (220kV)
| Monitored (Load growth driven) | South Morang Terminal Station (330/220 kV transformers) | Increased demand in Metropolitan Melbourne and increased import from New South Wales. | Augmentation | 37.644⁰ S 145.078⁰ E | Unavailable | Unavailable | Unavailable |  |  |  |  | 330/220kV |  |  | Replace the existing transformers with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $156M (includes H1 and H2 replacement, AusNet RIT-T) | Unavailable | Unavailable | 2028 (AusNet RIT-T) |  |  |  |  | N/A | Capacity limited by SMTS 330/220kV transformers. |  | 29kA (330kV) 25kA (220kV)
Eastern Victoria corridor | Monitored | Morwell Terminal Station | Customer load at risk (market benefit) | Augmentation | 38.257⁰ S 146.421⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Morwell MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install a fourth transformer at Morwell Terminal Station | Unavailable | Unavailable | Unavailable | 2031 | 7.6 MVA (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 390 MVA (summer N-1 import) 434 MVA (winter N-1 import) with 2 transformers and embedded generation | Capacity limited by MWTS supply transformers. | Unavailable from TCPR | 24kA (66kV) B14 19kA (66kV) B2 18kA (66kV) B3 | $3.48M in 2031 (TCPR) | $38,662/MWh (TCPR) | 89.9 MWh in 2031 (TCPR)
South West Victoria corridor | Monitored | Moorabool Terminal Station (500/220 kV transformers) | New generation connected to Western Victoria area and to relieve congestion in Western Victoria. | Augmentation | 38.037⁰ S 144.296⁰ E | Unavailable | Unavailable | Unavailable |  |  |  |  | 500/220kV |  |  | Options considered: Install an automatic generation runback control scheme. Install a third 500/220 kV transformer at Moorabool Terminal Station. | Unavailable | Unavailable | Unavailable | Unavailable | [5 empty] | Capacity limited by MLTS 500/220kV transformers. | Unavailable | 22kA (500kV) 36kA (220kV)
Eastern Victoria corridor |  | Hazelwood Terminal Station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 29kA
|  | Hazelwood Power Station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 36kA
|  | Jeeralang Terminal Station |  |  | 38.277⁰ S 146.424⁰ E | [7 empty] | 220kV | [14 empty] | 37kA
|  | Loy Yang Power Station |  |  | 38.256⁰ S 146.574⁰ E | [7 empty] | 500kV | [14 empty] | 30kA
|  | Yallourn Power Station |  |  | 38.174⁰ S 146.35⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
North East Victoria corridor |  | Bogong Terminal Station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 13kA
|  | Dartmouth Terminal Station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Dederang Terminal Station |  |  | 36.454⁰ S 146.991⁰ E | [7 empty] | 330kV | [14 empty] | 21kA
|  | Dederang Terminal Station |  |  | 36.454⁰ S 146.991⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Eildon Terminal Station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | McKay Creek Terminal Station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Mt Beauty Terminal Station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | West Kiewa Power Station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Wodonga Terminal Station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | Plumpton Renewable Terminal Station |  |  | 37.674⁰ S 144.734⁰ E | [7 empty] | 500kV | [14 empty] | 24kA
|  | Sydenham Terminal Station |  |  | 37.676⁰ S 144.747⁰ E | [7 empty] | 500kV | [14 empty] | 25kA
|  | East Rowville Terminal Station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 220kV | [14 empty] | 34kA
|  | Tyabb Terminal Station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 220kV | [14 empty] | 20kA
|  | Western Port Terminal Station - John Lysaght (JLA) |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Malvern Terminal Station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Springvale Terminal Station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Heatherton Terminal Station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Ringwood Terminal Station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Templestowe Terminal Station |  |  | 37.748⁰ S 145.171⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Thomastown Terminal Station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 220kV | [14 empty] | 31kA
|  | Richmond Terminal Station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Brunswick Terminal Station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 220kV | [14 empty] | 30kA
|  | West Melbourne Terminal Station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Fishermans Bend Terminal Station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Newport Terminal Station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Laverton North Power Station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Geelong Terminal Station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 220kV | [14 empty] | 30kA
Central North Victoria corridor |  | Bendigo Terminal Station |  |  | 36.784⁰ S 144.254⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Fosterville Terminal Station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Glenrowan Terminal Station |  |  | 36.494⁰ S 146.132⁰ E | [7 empty] | 220kV | [14 empty] | 13kA
|  | Goorambat East Terminal Station |  |  | 36.427⁰ S 145.926⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Pine Lodge Terminal Station |  |  | 36.341⁰ S 145.570⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Shepparton Terminal Station |  |  | 36.343⁰ S 145.415⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
North West Victoria corridor |  | Carwarp Terminal Station |  |  | 34.499⁰ S 142.235⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Kerang Terminal Station |  |  | 35.771⁰ S 143.934⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Kiamal Terminal Station |  |  | 35.030⁰ S 142.294⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Koorangie Terminal Station |  |  | 35.730⁰ S 143.753⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Red Cliffs Terminal Station |  |  | 34.292⁰ S 142.239⁰ E | [7 empty] | 220kV | [14 empty] | 13kA
|  | Wemen Terminal Station |  |  | 34.787⁰ S 142.524⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
South West Victoria corridor |  | Berrybank Terminal Station |  |  | 37.886⁰ S 143.453⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Blue Gum Substation |  |  | 38.061⁰ S 142.677⁰ E | [7 empty] | 500kV | [14 empty] | 15kA
|  | Cressy Terminal Station |  |  | 37.999⁰ S 143.752⁰ E | [7 empty] | 500kV | [14 empty] | 19kA
|  | Elaine Terminal Station |  |  | 37.730⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Gnarwarre Terminal Station |  |  | 38.147⁰ S 144.127⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Golden Plains Terminal Station |  |  | 37.972⁰ S 143.777⁰ E | [7 empty] | 220kV | [14 empty] | 20kA
|  | Haunted Gully Terminal Station |  |  | 38.008⁰ S 143.313⁰ E | [7 empty] | 500kV | [14 empty] | 15kA
|  | Heywood Terminal Station |  |  | 38.181⁰ S 141.639⁰ E | [7 empty] | 500kV | [14 empty] | 11kA
|  | Mortlake Terminal Station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 15kA
|  | Portland Substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Tarrone Terminal Station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 11kA
|  | Terang Terminal Station |  |  | 38.233⁰ S 142.932⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
Western Victoria corridor |  | Ararat Terminal Station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Ballarat Terminal Station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Bulgana Terminal Station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Crowlands Terminal Station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Horsham Terminal Station |  |  | 36.722⁰ S 142.248⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Murra Warra Terminal Station |  |  | 36.433⁰ S 142.320⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Waubra Terminal Station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Note 1: Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
Note 2: Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
Note 3: Priority limitations which are marked as (VTP actioned) or (committed project actioned) will include the same level of detailed data as for the monitored limitations. This is because the results of the VAPR modelling already factors in the completion of those future projects to address the limitation.
Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.

## Altona_Brooklyn MD forecast
Station: ATS/BLTS
Import | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 342.2 | 429.3 | 519.9 | 568.8 | 611.5 | 668.9 | 761.1 | 918.5 | 1043.7 | 1144.6
50th percentile Winter Maximum Demand (MVA) | 357.3 | 450.8 | 521.7 | 573.5 | 623.4 | 685.8 | 783.3 | 946.2 | 1075.6 | 1181.2
10th percentile Summer Maximum Demand (MVA) | 379.6 | 466.2 | 559.4 | 610 | 651.1 | 708 | 800.5 | 958.5 | 1084.1 | 1185
10th percentile Winter Maximum Demand (MVA) | 379 | 472.8 | 544.2 | 595.9 | 645.4 | 707.9 | 805.5 | 968.9 | 1098 | 1203.4
Note : Data from 2025 TCPR

## Altona West MD forecast
Station: ATS West
Import | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 290.7 | 322.6 | 345.8 | 422.2 | 442 | 452.7 | 461.8 | 469.3 | 474.3 | 478.1
50th percentile Winter Maximum Demand (MVA) | 250.89 | 311 | 338.42 | 402.29 | 417.72 | 436.89 | 452.45 | 464.88 | 475.59 | 485.31
10th percentile Summer Maximum Demand (MVA) | 322.1 | 353.3 | 377.3 | 452.9 | 472.3 | 482.5 | 493 | 501.5 | 507.1 | 511
10th percentile Winter Maximum Demand (MVA) | 262.13 | 320.38 | 347.42 | 413.03 | 429.01 | 449.06 | 465.07 | 478.17 | 490.08 | 500.04
Note : Data from 2025 TCPR

## Cranbourne MD forecast
Station: CBTS 66 kV
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 594.3 | 621 | 630.2 | 642.1 | 647.7 | 655 | 663.5 | 679.4 | 686.6 | 696.1
50th percentile Winter Maximum Demand (MVA) | 518.7 | 535.5 | 554.5 | 569.9 | 586.5 | 606.7 | 625.6 | 640.3 | 654 | 668.4
10th percentile Summer Maximum Demand (MVA) | 639.9 | 662 | 669.4 | 680 | 686.7 | 692.2 | 704.5 | 715.6 | 729.4 | 740.4
10th percentile Winter Maximum Demand (MVA) | 539.4 | 556.4 | 575 | 589.2 | 606 | 626.9 | 645.2 | 656.4 | 673.8 | 686.4
Note : Data from 2025 TCPR

## Deer Park MD forecast
Station: DPTS 66 kV
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 367.9 | 466.1 | 542.2 | 591.2 | 625.5 | 643.7 | 657.5 | 671.5 | 682.9 | 693.5
50th percentile Winter Maximum Demand (MVA) | 351.3 | 465.9 | 532.7 | 586.5 | 624.3 | 648.7 | 672.4 | 694.9 | 714.6 | 733.2
10th percentile Summer Maximum Demand (MVA) | 421.9 | 525.3 | 601.7 | 651.9 | 686.9 | 706 | 721.6 | 736.6 | 749.1 | 761.1
10th percentile Winter Maximum Demand (MVA) | 384.6 | 498.7 | 566.4 | 620.1 | 657 | 681.5 | 707.3 | 730.2 | 749.4 | 768.6
Note : Data from 2025 TCPR

## Keilor MD forecast
Station: KTS 66 kV (B1,2,5 transformer group)
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 375.255 | 427.1248 | 472.1207 | 509.4643 | 572.4169 | 661.5644 | 736.4994 | 810.87 | 868.6334 | 907.1015
50th percentile Winter Maximum Demand (MVA) | 327.1249 | 384.171 | 438.0243 | 481.459 | 550.8349 | 644.7085 | 722.7077 | 798.8769 | 857.3264 | 898.5309
10th percentile Summer Maximum Demand (MVA) | 424.0935 | 476.3096 | 522.6941 | 559.8202 | 623.091 | 712.8105 | 788.2339 | 863.482 | 920.7988 | 958.9891
10th percentile Winter Maximum Demand (MVA) | 355.8813 | 413.4672 | 467.9101 | 511.7003 | 581.4046 | 675.7361 | 753.835 | 830.1341 | 888.5204 | 929.7951
Note : Data from 2025 TCPR
Station: KTS 66 kV (B3,4 transformer group)
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 243.012 | 251.8622 | 294.2493 | 372.3517 | 450.8816 | 553.3928 | 667.0531 | 760.873 | 835.7303 | 890.649
50th percentile Winter Maximum Demand (MVA) | 237.4568 | 250.4612 | 298.6805 | 382.0033 | 466.0459 | 573.0858 | 690.2578 | 786.3374 | 863.385 | 921.6706
10th percentile Summer Maximum Demand (MVA) | 266.9178 | 276.3344 | 318.4893 | 396.6908 | 474.9114 | 577.7935 | 691.9725 | 785.8046 | 860.8674 | 915.9338
10th percentile Winter Maximum Demand (MVA) | 235.384 | 248.408 | 296.6571 | 380.0519 | 463.9536 | 570.9367 | 687.7093 | 784.0469 | 861.2412 | 919.4176
Note : Data from 2025 TCPR

## Morwell MD forecast
Station: MWTS 66 kV
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 446.4 | 455.8 | 466.2 | 470.5 | 471.3 | 478.9 | 479.7 | 487 | 494.2 | 494
50th percentile Winter Maximum Demand (MVA) | 461.1 | 477.9 | 489.4 | 497.3 | 516 | 530.6 | 580.3 | 593 | 558.9 | 591.8
10th percentile Summer Maximum Demand (MVA) | 475.2 | 485.2 | 494 | 498.6 | 495.8 | 503.5 | 511.5 | 516.2 | 521 | 514.6
10th percentile Winter Maximum Demand (MVA) | 473 | 488.6 | 500.2 | 523.9 | 551.2 | 535.5 | 594.3 | 598.7 | 619.3 | 606.7
Note : Data from 2025 TCPR

## South Morang MD forecast
Station: SMTS 66 kV
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 431.4 | 460.2 | 481.1 | 510.2 | 557.3 | 644.7 | 753.3 | 896.5 | 1014.6 | 1105.7
50th percentile Winter Maximum Demand (MVA) | 409.1 | 434.3 | 476.8 | 499.5 | 562.4 | 660.8 | 803.6 | 963.5 | 1092.3 | 1184.2
10th percentile Summer Maximum Demand (MVA) | 459.3 | 486.5 | 507.4 | 534.4 | 584.2 | 670.5 | 779.6 | 931.6 | 1049.7 | 1139.8
10th percentile Winter Maximum Demand (MVA) | 422.4 | 448.4 | 491.9 | 511.8 | 576.7 | 677.1 | 815.7 | 976.3 | 1112.4 | 1205.1
Note : Data from 2025 TCPR

## Thomastown MD forecast
Station: TTS 66 kV (B3,4)
Year | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
50th percentile Summer Maximum Demand (MVA) | 279.8731 | 288.5084 | 299.1631 | 316.9298 | 326.71 | 356.7678 | 409.4468 | 449.7362 | 515.3181 | 610.0155
50th percentile Winter Maximum Demand (MVA) | 273.0632 | 287.9276 | 304.8473 | 328.3411 | 344.3571 | 376.907 | 431.4987 | 472.119 | 537.4797 | 633.9118
10th percentile Summer Maximum Demand (MVA) | 299.8128 | 307.8154 | 317.6724 | 335.5361 | 345.0549 | 375.2927 | 428.6487 | 469.3539 | 535.0648 | 629.7329
10th percentile Winter Maximum Demand (MVA) | 290.207 | 304.9258 | 321.6047 | 344.8072 | 360.6227 | 393.3962 | 448.3824 | 488.8243 | 553.9022 | 649.8715
Note : Data from 2025 TCPR