## Disclaimer
Disclaimer
This publication has been prepared by VicGrid Body Corporate (VicGrid). VicGrid has made reasonable
efforts to ensure the quality of the information contained in this publication. While reasonable effort has been
made to check the information contained in this document, VicGrid cannot guarantee that information,
forecasts and assumptions are current, accurate, complete or appropriate for use in all circumstances.
Anyone proposing to use the information in this publication should independently verify its accuracy and
suitability for its intended use, and obtain independent expert advice.
To the extent permitted by law, VicGrid disclaims all liability for any error, omission, loss or other
consequence arising from reliance on any information, representation, statement, opinion or matter
(express or implied) contained in or derived from this document. Nothing in this publication affects the
operation of the National Electricity (Victoria) Act 2005, the National Electricity Rules or the
National Electricity (Victoria) Law.

## Introduction
Victorian Declared Shared Network rating and loading information
This workbook presents declared shared network (DSN) rating1 and loading information at the time of the maximum demand snapshot presented in Chapter 4 of the 2025 Victorian Network Performance and Insight Report (VNPIR).
The "Maximum demand 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the maximum demand snapshot.
The "Maximum demand 2" worksheet presents a summary of Interconnector power flows and limits at the time of the maximum demand snapshot.
The "High export to NSW 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the high power flow from Victoria to NSW snapshot. Only Northern Corridor elements are shown for this snapshot as this is the only region where DSN elements tend to be more heavily loaded during high export from Victoria, rather than during high Victorian demand.
The "High export to NSW 2" worksheet presents a summary of the reactive power adequacy, as well as Interconnector power flows and limits at the time of the high power flow from Victoria to NSW snapshot.
The "High Wind 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the high wind snapshot.
The "High Wind 2" worksheet presents a summary of Interconnector power flows and limits at the time of the high wind snapshot.
The (N) loading for an asset presents its % loading under system normal condition, based on the asset’s continuous rating.
The (N-1) loading of an asset presents its % loading following the worst single credible contingency, based on the asset’s short term rating. The reported short-term ratings for transmission lines represent the 15 minute ratings.
Rating types are shown in the tables as “D” (dynamic rating), “D/W” (dynamic rating with wind monitoring), and “S” (static rating).
Dynamic ratings (D) are used in real time by AEMO system operators, calculated by taking into account the ambient temperature and a solar heating factor calculation based on the date and time. For lines equipped with wind monitoring facilities (D/W), the calculation of dynamic ratings also takes into account the actual wind speed, otherwise a standard wind speed of 0.6 m/s is assumed.
The rating for equipment with static ratings (S) is based on ambient temperatures that assume a wind speed of 0.6 m/s. Short-term ratings are not available for some lines with static ratings, in which case, the short-term rating is equal to the continuous rating.
[1] AEMO. AEMO transmission equipment ratings. Available at https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/data-nem/network-data/transmission-equipment-ratings

## Maximum demand 1
Table 1 — Maximum demand snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MW) | Continuous loading (N) MVAr | MVA | Short–term rating* (N–1) (MVA) | Short-term loading (N-1) (MW) | MVAr | MVA | Rating type | (N) loading | (N–1) loading | Critical contingency
Eastern Corridor | 500 kV | Hazelwood 500kV - Loy Yang 500kV 1 | 2698 | 1104.3331 | 34.8961 | 1104.8843 | 2698 | 1656.3989 | 62.3507 | 1658 | D | 41 | 61 | Hazelwood 500kV - Loy Yang 500kV 2
|  | Hazelwood 500kV - Loy Yang 500kV 2 | 2764 | 1089.4382 | 35.1701 | 1090.0058 | 3200 | 1645.3003 | 62.5938 | 1646 | D | 39 | 51 | Hazelwood 500kV - Loy Yang 500kV 1
|  | Hazelwood 500kV - Loy Yang 500kV 3 | 2764 | 1074.9379 | 35.4503 | 1075.5223 | 3189 | 1623.3971 | 63.0022 | 1625 | D | 39 | 51 | Hazelwood 500kV - Loy Yang 500kV 1
|  | Hazelwood 500kV - South Morang 500kV 1 | 2529 | 780.477 | 30.3741 | 781.0678 | 2529 | 1088.7102 | 22.5266 | 1089 | S | 31 | 43 | Cranbourne 500kV - Hazelwood 500kV 1
|  | Hazelwood 500kV - South Morang 500kV 2 | 2529 | 780.9667 | 30.3688 | 781.557 | 2529 | 1089.3945 | 22.5508 | 1090 | S | 31 | 43 | Cranbourne 500kV - Hazelwood 500kV 1
|  | Hazelwood 500kV - Rowville 500kV | 3097 | 989.377 | 24.1972 | 989.6728 | 3097 | 1481.2166 | 74.0886 | 1483 | S | 32 | 48 | Cranbourne 500kV - Hazelwood 500kV 1
|  | Cranbourne 500kV - Hazelwood 500kV | 3097 | 1108.6338 | 2.7305 | 1108.6372 | 3097 | 1551.7764 | 90.2027 | 1554 | S | 36 | 50 | Hazelwood 500kV - Rowville 500kV 1
| 220 kV | Rowville 220kV - Yallourn 220kV 5 | 227 | 92.4883 | 10.9167 | 93.1304 | 250 | 138.3012 | 15.0933 | 139 | D/W | 41 | 56 | Hazelwood 220kV - Yallourn 220kV 1
|  | Rowville 220kV - Yallourn 220kV 6 | 227 | 136.658 | 18.9641 | 137.9675 | 250 | 195.2499 | 13.4344 | 196 | D/W | 61 | 78 | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Yallourn 220kV 7 | 227 | 139.3887 | 19.5719 | 140.7561 | 250 | 199.1686 | 14.0288 | 200 | D/W | 62 | 80 | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Yallourn 220kV 8 | 227 | 139.3887 | 19.5719 | 140.7561 | 250 | 199.1686 | 14.0288 | 200 | D/W | 62 | 80 | Rowville 500/220kV A1 Transformer
|  | Hazelwood 220kV - Yallourn 220kV 1 | 360 | 142.9242 | 20.44 | 144.3784 | 398 | 190.7243 | 25.6328 | 192 | D | 40 | 48 | Rowville 500/220kV A2 Transformer
|  | Hazelwood 220kV - Yallourn 220kV 2 | 360 | 305.3076 | 97.2823 | 320.4319 | 459 | 305.3076 | 97.2823 | 320 | D | 89 | 70 | No N-1 contingency for this line
|  | Hazelwood 220kV - Rowville 220kV 1 | 231 | 71.2572 | 10.3212 | 72.0008 | 252 | 95.0151 | 13.8281 | 96 | D/W | 31 | 38 | Rowville 500/220kV A2 Transformer
|  | Hazelwood 220kV - Rowville 220kV 2 | 231 | 71.3365 | 10.3048 | 72.077 | 252 | 95.1205 | 13.8196 | 96 | D/W | 31 | 38 | Rowville 500/220kV A2 Transformer
|  | Hazelwood 220kV - Morwell 220kV | 234 | 44.6533 | 23.1754 | 50.3092 | 294 | 84.7856 | 39.7659 | 94 | S | 21 | 32 | Jeeralang 220kV - Morwell 220kV 1
|  | Jeeralang 220kV - Morwell 220kV 1 | 349 | 63.4018 | 20.408 | 66.6054 | 349 | 92.6978 | 35.3501 | 99 | S | 19 | 28 | Hazelwood 220kV - Morwell 220kV
|  | Jeeralang 220kV - Morwell 220kV 2 | 349 | 32.6192 | 14.4532 | 35.6778 | 349 | 95.475 | 22.0596 | 98 | S | 10 | 28 | Latrobe BESS unit
|  | Hazelwood 220kV - Jeeralang 220kV 1 | 696 | 37.5826 | 15.0059 | 40.4676 | 696 | 51.5768 | 20.0702 | 55 | D | 6 | 8 | Hazelwood 220kV - Jeeralang 220kV 2
|  | Hazelwood 220kV - Jeeralang 220kV 2 | 696 | 36.7846 | 14.5952 | 39.5743 | 696 | 50.8933 | 19.7095 | 55 | D | 6 | 8 | Hazelwood 220kV - Jeeralang 220kV 1
|  | Hazelwood 220kV - Jeeralang 220kV 3 | 359 | 30.4036 | 13.3031 | 33.1866 | 395 | 42.0751 | 18.0332 | 46 | D | 9 | 12 | Hazelwood 220kV - Jeeralang 220kV 1
|  | Hazelwood 220kV - Jeeralang 220kV 4 | 359 | 30.4036 | 13.3031 | 33.1866 | 383 | 42.0751 | 18.0332 | 46 | D | 9 | 12 | Hazelwood 220kV - Jeeralang 220kV 1
| 500/220 kV | Rowville 500/220kV A1 Transformer | 1000 | 942.7294 | 187.5215 | 961.1987 | 1500 | 1093.0242 | 231.2453 | 1117 | S | 96 | 74 | Rowville 500/220kV A2 Transformer
|  | Rowville 500/220kV A2 Transformer | 1000 | 716.598 | 182.8977 | 739.5703 | 1500 | 1081.0876 | 213.8377 | 1102 | S | 74 | 73 | Cranbourne 500/220kV A1 Transformer
|  | Hazelwood 500/220kV A1 Transformer | 600 | 97.6507 | 47.1223 | 108.4258 | 638 | 130.4022 | 58.4794 | 143 | S | 18 | 22 | Hazelwood 500/220kV A3 Transformer
|  | Hazelwood 500/220kV A2 Transformer | 600 | 98.682 | 47.6899 | 109.6014 | 638 | 131.7819 | 59.1889 | 144 | S | 18 | 23 | Hazelwood 500/220kV A3 Transformer
|  | Hazelwood 500/220kV A3 Transformer | 600 | 99.0102 | 47.9128 | 109.9939 | 638 | 132.0739 | 59.4041 | 145 | S | 18 | 23 | Hazelwood 500/220kV A2 Transformer
|  | Hazelwood 500/220kV A4 Transformer | 600 | 98.6656 | 47.7224 | 109.6007 | 638 | 131.7615 | 59.2322 | 144 | S | 18 | 23 | Hazelwood 500/220kV A3 Transformer
South–West Corridor | 500 kV | Heywood 500kV - Tarrone 500kV | 2495 | 357.9251 | 34.6927 | 359.6025 | 2495 | 531.5 | 59.9 | 535 | S | 14 | 21 | Mortlake 500kV - Heywood 500 kV
|  | Haunted Gully 500kV - cressy 500kV | 2495 | 426.957 | 71.6262 | 432.9233 | 2495 | 985.6855 | 87.2799 | 990 | S | 17 | 40 | Cressy 500kV - Moorabool 500kV 1
|  | Cressy 500kV - Moorabool 500kV 1 | 2495 | 452.9834 | 15.7386 | 453.2568 | 2495 | 887.4688 | 62.3943 | 890 | S | 18 |  | Cressy 500kV - Moorabool 500kV 2
|  | Cressy 500kV - Moorabool 500kV 2 | 2495 | 438.5424 | 30.3769 | 439.5932 | 2495 | 1086.9919 | 76.3508 | 1090 | S | 18 |  | Cressy 500kV - Moorabool 500kV 1
|  | Cressy 500kV - Mortlake 500kV | 2495 | 355.784 | 87.7443 | 366.4442 | 2495 | 987.1507 | 83.3027 | 991 | S | 15 | 40 | Haunted Gully 500kV - cressy 500kV
|  | Heywood 500kV - Mortlake 500kV | 2495 | 176.9402 | 80.3038 | 194.3104 | 2495 | 312.4669 | 136.2779 | 341 | S | 8 | 14 | Heywood 500kV - Tarrone 500kV and Alcoa Portland 500kV - Heywood 500kV 1
|  | Alcoa Portland 500kV - Heywood 500kV 1 | 1386 | 114.2327 | 164.5536 | 200.3172 | 1386 | 227.5133 | 221.9042 | 318 | S | 14 | 23 | Alcoa Portland 500kV - Heywood 500kV 2
|  | Alcoa Portland 500kV - Heywood 500kV 2 | 1386 | 113.5393 | 163.6091 | 199.146 | 1386 | 227.5066 | 221.8766 | 318 | S | 14 | 23 | Alcoa Portland 500kV - Heywood 500kV 1
| 275 kV | South East 275kV - Heywood 275kV 1 | 497 | 153.4091 | 13.1904 | 153.9751 | 595 | 292.371 | 20.1333 | 293 | D | 31 | 49 | South East 275kV - Heywood 275kV 2
|  | South East 275kV - Heywood 275kV 2 | 497 | 153.4091 | 13.1904 | 153.9751 | 595 | 292.371 | 20.1333 | 293 | D | 31 | 49 | South East 275kV - Heywood 275kV 1
| 500/275 kV | Heywood 500/275kV M1 Transformer | 300 | 101.9 | -48.1 | 112.6819 | 525 | 152.4 | -66.2 | 166 | S | 38 | 32 | Heywood 500/275kV M3 Transformer
|  | Heywood 500/275kV M2 Transformer | 300 | 101.9 | -48.1 | 112.6819 | 525 | 152.4 | -66.2 | 166 | S | 38 | 32 | Heywood 500/275kV M3 Transformer
|  | Heywood 500/275kV M3 Transformer | 370 | 103.0823 | 50.9264 | 114.9759 | 525 | 153.2196 | 71.9051 | 169 | S | 31 | 32 | Heywood 500/275kV M2 Transformer
Northern Corridor | 330 kV | Dederang 330kV - Wodonga 330kV | 743 | 263.7792 | 56.2137 | 269.7025 | 743 | 456.603 | 8.8762 | 457 | D | 36 | 62 | Plumpton 500kV - Sydham 500kV
|  | Dederang 330kV - Murray 330kV 1 | 943 | 484.735 | 158.3817 | 509.9537 | 1017 | 826.5731 | 302.3582 | 880 | D | 54 | 87 | Dederang 330kV - Murray 330kV 2
|  | Dederang 330kV - Murray 330kV 2 | 943 | 477.8368 | 162.4348 | 504.691 | 1017 | 822.8842 | 309.423 | 879 | D | 54 | 86 | Dederang 330kV - Murray 330kV 1
|  | Dederang 330kV - South Morang 330kV 1 | 823 | 342.6479 | 66.697 | 349.0789 | 932 | 689.7527 | 263.5345 | 738 | D | 42 | 79 | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330kV - South Morang 330kV 2 | 823 | 613.6287 | 290.6984 | 679.0035 | 932 | 898.3602 | 660.786 | 1115 | D | 83 | 120 | Plumpton 500kV - Sydham 500kV
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 204 | 44.81 | 35.9304 | 57.4363 | 204 | 266.3534 | 32.2218 | 268 | D | 28 | 131 | Eildon 220kV - Thomastown 220kV
|  | Dederang 220kV - Mount Beauty 220kV 2 | 204 | 44.81 | 35.9304 | 57.4363 | 204 | 266.3534 | 32.2218 | 268 | D | 28 | 131 | Eildon 220kV - Thomastown 220kV
|  | Dartmouth 220kV - Mount Beauty 220kV | 230 | 152.3584 | 7.6457 | 152.5501 | 230 | 152.3584 | 7.6457 | 153 | D | 66 | 67 | No N-1 contingency for this line
|  | Bogong 220kV - Mount Beauty 220kV | 536 | 148.5049 | 15.21 | 149.2818 | 536 | 148.5049 | 15.21 | 149 | D | 28 | 28 | No N-1 contingency for this line
|  | Mount Beauty 220kV - West Kiewa 220kV | 97 | 46.9306 | 5.0466 | 47.2012 | 97 | 46.9306 | 5.0466 | 47 | S | 49 | 48 | No N-1 contingency for this line
|  | Eildon 220kV - Thomastown 220kV | 408 | 436.8388 | 20.6107 | 437.3248 | 408 | 612.4547 | 49.8512 | 614 | D | 107 | 150 | Dederang 330kV - South Morang 330kV 2
|  | Eildon 220kV - Mount Beauty 220kV 1 | 204 | 181.6902 | 10.0717 | 181.9691 | 204 | 277.847 | 26.6024 | 279 | D | 89 | 137 | Dederang 330kV - South Morang 330kV 2
|  | Eildon 220kV - Mount Beauty 220kV 2 | 204 | 181.6902 | 10.0717 | 181.9691 | 204 | 277.847 | 26.6024 | 279 | D | 89 | 137 | Dederang 330kV - South Morang 330kV 2
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 84.8939 | 21.9766 | 87.6924 | 400 | 196.7945 | 7.1946 | 197 | S | 26 | 49 | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330/220kV H2 Transformer | 340 | 75.5463 | 19.2677 | 77.9647 | 400 | 174.9859 | 5.7685 | 175 | S | 23 | 44 | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330/220kV H3 Transformer | 240 | 72.7029 | 14.5303 | 74.1407 | 400 | 166.4621 | 3.2476 | 166 | S | 31 | 42 | Dederang 330kV - South Morang 330kV 2
Greater Melbourne and Geelong | 500 kV | Moorabool 500kV - Sydenham 500kV 1 | 2445 | 17.3 | -43.8 | 47.0928 | 2445 | 31.9 | -50.9 | 60 | S | 2 | 2 | Moorabool 500kV - Sydenham 500kV 2
|  | Moorabool 500kV - Sydenham 500kV 2 | 2445 | 17.3 | -43.8 | 47.0928 | 2445 | 31.9 | -50.9 | 60 | S | 2 | 2 | Moorabool 500kV - Sydenham 500kV 1
|  | Keilor 500kV - Sydenham 500kV | 2799 | 911.6067 | 176.726 | 928.5789 | 2799 | 1478.4512 | 259.5646 | 1501 | S | 33 | 54 | Keilor 500kV - South Morang 500kV
|  | Keilor 500kV - South Morang 500kV | 2598 | 638.3821 | 95.1176 | 645.4294 | 2598 | 1404.8821 | 244.8196 | 1426 | S | 25 | 55 | Keilor 500kV - Sydenham 500kV
|  | South Morang 500kV - Sydenham 500kV 1 | 2598 | 179.3079 | 32.5744 | 182.2427 | 2598 | 467.2256 | 61.6536 | 471 | S | 7 | 18 | Keilor 500kV - South Morang 500kV
|  | South Morang 500kV - Sydenham 500kV 2 | 2651 | 176.4917 | 33.1244 | 179.5733 | 2651 | 459.8701 | 62.0468 | 464 | S | 7 | 18 | Keilor 500kV - South Morang 500kV
|  | Rowville 500kV - South Morang 500kV | 3097 | 364.7402 | 102.796 | 378.9491 | 3097 | 873.2218 | 65.1223 | 876 | S | 12 | 28 | Cranbourne 500kV - Hazelwood 500kV
|  | Cranbourne 500kV - Rowville 500kV | 2771 | 317.0596 | 73.0592 | 325.3681 | 2771 | 990.5263 | 31.8737 | 991 | S | 12 | 36 | Cranbourne 500/220kV A1 Transformer
| 220 kV | Geelong 220kV - Moorabool 220kV 1 | 720 | 374.8057 | 84.341 | 384.178 | 720 | 713.5482 | 170.289 | 734 | D | 53 | 102 | Geelong 220kV - Moorabool 220kV 2
|  | Geelong 220kV - Moorabool 220kV 2 | 720 | 374.8057 | 84.341 | 384.178 | 720 | 713.5482 | 170.289 | 734 | D | 53 | 102 | Geelong 220kV - Moorabool 220kV 1
|  | Geelong 220kV - Keilor 220kV 1 | 204 | 109.9059 | 3.4062 | 109.9586 | 204 | 168.8605 | 15.1722 | 170 | D/W | 54 | 83 | Keilor 500/220kV A4 Transformer
|  | Deer Park 220kV - Geelong 220kV 2 | 204 | 167.7559 | 29.8812 | 170.3963 | 204 | 341.4971 | 217.9137 | 405 | D/W | 84 | 199 | Deer Park 220kV - Keilor 220kV 2
|  | Deer Park 220kV - Keilor 220kV 2 | 204 | 173.431 | 99.8148 | 200.1033 | 204 | 338.1 | 137.9 | 365 | D/W | 98 | 179 | Geelong 220kV - Deer Park 220kV 1
|  | Geelong 220kV - Keilor 220kV 3 | 204 | 109.9879 | 3.4239 | 110.0412 | 204 | 168.9862 | 15.2018 | 170 | D/W | 54 | 83 | Keilor 500/220kV A4 Transformer
|  | Altona 220kV - Keilor 220kV | 720 | 276.0284 | 9.1831 | 276.1811 | 876 | 452.5345 | 52.5848 | 456 | D | 38 | 52 | Brooklyn 220kV - Keilor 220kV
|  | Brooklyn 220kV - Keilor 220kV | 720 | 229.7298 | 40.8758 | 233.338 | 838 | 457.8735 | 64.2445 | 462 | D | 32 | 55 | Altona 220kV - Keilor 220kV
|  | Altona 220kV - Brooklyn 220kV | 720 | 89.6968 | 70.6382 | 114.1721 | 792 | 359.099 | 62.1497 | 364 | D | 16 | 46 | Altona 220kV - Keilor 220kV
|  | Brooklyn 220kV - Newport 220kV | 698 | 92.5344 | 1.5259 | 92.547 | 698 | 420.8011 | 47.3334 | 423 | D | 13 | 61 | Fishermans Bend 220kV - Newport 220kV
|  | Brooklyn 220kV - Fishermans Bend 220kV | 720 | 64.8128 | 6.8868 | 65.1776 | 823 | 143.8893 | 18.6708 | 145 | D | 9 | 18 | Keilor 500/220kV A3 Transformer
|  | Fishermans Bend 220kV - Newport 220kV | 720 | 328.0492 | 72.5107 | 335.9673 | 720 | 420.4482 | 76.4801 | 427 | D | 47 | 59 | Brooklyn 220kV - Newport 220kV
|  | Fishermans Bend 220kV - West Melbourne 220kV 1 | 349 | 26.7175 | 30.6664 | 40.6725 | 420 | 135.5869 | 48.5613 | 144 | D | 12 | 34 | Newport generating unit
|  | Fishermans Bend 220kV - West Melbourne 220kV 2 | 349 | 26.7175 | 30.6664 | 40.6725 | 420 | 135.5869 | 48.5613 | 144 | D | 12 | 34 | Newport generating unit
|  | Keilor 220kV - West Melbourne 220kV 1 | 686 | 81.4515 | 32.5611 | 87.7187 | 686 | 244.4108 | 45.3507 | 249 | D | 13 | 36 | Newport generating unit
|  | Keilor 220kV - West Melbourne 220kV 2 | 686 | 81.1838 | 32.4277 | 87.4206 | 686 | 243.591 | 45.1187 | 248 | D | 13 | 36 | Newport generating unit
|  | Keilor 220kV - Thomastown 220kV 1 | 462 | 211.8813 | 31.5899 | 214.2233 | 478 | 536.2103 | 123.407 | 550 | S | 46 | 115 | South Morang 330/220kV H3 Transformer
|  | Keilor 220kV - Thomastown 220kV 2 | 542 | 123.2665 | 123.3102 | 174.3561 | 687 | 321.1437 | 89.1468 | 333 | S | 32 | 48 | Eildon 220kV - Thomastown 220kV
|  | South Morang 220kV - Thomastown 220kV 1 | 549 | 375.567 | 162.4331 | 409.1883 | 604 | 518.1683 | 179.7061 | 548 | S | 75 | 91 | Rowville 500/220kV A1 Transformer
|  | South Morang 220kV - Thomastown 220kV 2 | 549 | 419.144 | 184.2933 | 457.8709 | 604 | 560.8615 | 204.7534 | 597 | S | 83 | 99 | Rowville 500/220kV A1 Transformer
|  | Brunswick 220kV - Thomastown 220kV 1 | 549 | 22.5459 | 105.5193 | 107.901 | 643 | 284.1743 | 218.9522 | 359 | D | 20 | 56 | South Morang 220kV - Thomastown 220kV 2
|  | Brunswick 220kV - Thomastown 220kV 2 | 698 | 467.9438 | 38.1595 | 469.4971 | 800 | 620.8258 | 22.8343 | 621 | D | 67 | 78 | South Morang 220kV - Thomastown 220kV 2
|  | Ringwood 220kV - Thomastown 220kV | 616 | 353.6618 | 29.9789 | 354.9301 | 616 | 752.1401 | 61.0771 | 755 | D | 58 | 123 | Rowville 500/220kV A1 Transformer
|  | Templestowe 220kV - Thomastown 220kV | 616 | 259.8629 | 90.1118 | 275.0434 | 616 | 640.5592 | 151.7642 | 658 | D | 45 | 107 | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Templestowe 220kV | 720 | 101.9607 | 39.1815 | 109.2299 | 766 | 360.8284 | 131.9968 | 384 | D | 15 | 50 | Templestowe 220kV - Thomastown 220kV
|  | Rowville 220kV - Thomastown 220kV | 550 | 21.854 | 24.9315 | 33.1538 | 605 | 150.163 | 38.5095 | 155 | D | 6 | 26 | Brunswick 220kV - Thomastown 220kV 2
|  | Ringwood 220kV - Rowville 220kV | 664 | 211.0732 | 108.5632 | 237.356 | 664 | 562.7913 | 142.1368 | 580 | D | 36 | 87 | Ringwood 220kV - Thomastown 220kV
|  | Malvern 220kV - Rowville 220kV 1 | 204 | 120.283 | 38.0297 | 126.1517 | 237 | 241.199 | 82.6557 | 255 | D | 62 | 108 | Malvern 220kV - Rowville 220kV 2
|  | Malvern 220kV - Rowville 220kV 2 | 204 | 120.2748 | 38.0813 | 126.1595 | 237 | 241.1957 | 82.6547 | 255 | D | 62 | 108 | Malvern 220kV - Rowville 220kV 1
|  | Rowville 220kV - Springvale 220kV 1 | 698 | 398.613 | 5.9558 | 398.6575 | 835 | 798.5674 | 29.6673 | 799 | D/W | 57 | 96 | Rowville 220kV - Springvale 220kV 2
|  | Rowville 220kV - Springvale 220kV 2 | 698 | 398.613 | 5.9558 | 398.6575 | 835 | 798.5674 | 29.6673 | 799 | D/W | 57 | 96 | Rowville 220kV - Springvale 220kV 1
|  | Richmond 220kV - Rowville 220kV 1 | 540 | 227.2246 | 7.232 | 227.3396 | 765 | 350.4849 | 13.3245 | 351 | D | 42 | 46 | Thomastown 220kV - Brunswick 220kV 2
|  | Richmond 220kV - Rowville 220kV 2 | 540 | 225.7523 | 7.8381 | 225.8883 | 765 | 349.312 | 4.5228 | 349 | D | 42 | 46 | Richmond 220kV - Rowville 220kV 1
|  | Heatherton 220kV - Springvale 220kV 1 | 349 | 192.2623 | 13.4123 | 192.7296 | 405 | 385.2212 | 33.9019 | 387 | D | 55 | 96 | Heatherton 220kV - Springvale 220kV 2
|  | Heatherton 220kV - Springvale 220kV 2 | 349 | 192.2623 | 13.4123 | 192.7296 | 405 | 385.2212 | 33.9019 | 387 | D | 55 | 96 | Heatherton 220kV - Springvale 220kV 1
|  | East Rowville 220kV - Rowville 220kV 1 | 698 | 237.2549 | 130.5016 | 270.7776 | 809 | 630.1547 | 128.0581 | 643 | D | 39 | 79 | Cranbourne 500/220kV A1 Transformer
|  | East Rowville 220kV - Rowville 220kV 2 | 698 | 237.2549 | 130.5016 | 270.7776 | 798 | 630.1547 | 128.0581 | 643 | D | 39 | 81 | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - East Rowville 220kV 1 | 720 | 18.0057 | 143.3937 | 144.5198 | 760 | 410.7306 | 132.8897 | 432 | D | 20 | 57 | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - East Rowville 220kV 2 | 720 | 18.0057 | 143.3937 | 144.5198 | 760 | 410.7306 | 132.8897 | 432 | D | 20 | 57 | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - Tyabb 220kV 1 | 543 | 151.1104 | 33.7326 | 154.8297 | 543 | 303.2422 | 96.9041 | 318 | D | 29 | 59 | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 2
|  | Cranbourne 220kV - Tyabb 220kV 2 | 543 | 151.1104 | 33.7326 | 154.8297 | 543 | 303.2422 | 96.9041 | 318 | D | 29 | 59 | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 1
|  | John Lysaght 220kV - Tyabb 220kV 1 | 183 | 10.3141 | 5.3363 | 11.6128 | 183 | 20.6261 | 10.6705 | 23 | S | 6 | 13 | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 2
|  | John Lysaght 220kV - Tyabb 220kV 2 | 183 | 10.3141 | 5.3363 | 11.6128 | 183 | 20.6282 | 10.6727 | 23 | S | 6 | 13 | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 1
|  | Brunswick 220kV - Richmond 220kV | 450 | 21.0615 | 84.9353 | 87.5076 | 650 | 249.925 | 71.9458 | 260 | S | 19 | 40 | Cranbourne 500/220kV A1 Transformer
| 500/220 kV | Keilor 500/220kV A2 Transformer | 750 | 524.2145 | 90.0211 | 531.8878 | 810 | 723.5027 | 174.6579 | 744 | S | 71 | 92 | Keilor 500/220kV A4 Transformer
|  | Keilor 500/220kV A3 Transformer | 750 | 498.899 | 91.5712 | 507.2332 | 810 | 644.5894 | 127.5172 | 657 | S | 68 | 81 | Rowville 500/220kV A1 Transformer
|  | Keilor 500/220kV A4 Transformer | 750 | 526.8753 | 90.2512 | 534.5492 | 810 | 725.8076 | 174.6646 | 747 | S | 71 | 92 | Keilor 500/220kV A2 Transformer
|  | Cranbourne 500/220kV A1 Transformer | 1000 | 782.1761 | 78.473 | 786.1027 | 1500 | 1062.5852 | 102.185 | 1067 | S | 79 | 71 | Rowville 500/220kV A2 Transformer
| 500/330 kV | South Morang 500/330kV F1 Transformer | 1000 | 93.9 | 92.5 | 131.8084 | 1500 | 235.8 | 112.9 | 261 | S | 13 | 17 | Rowville 500/220kV A1 Transformer
|  | South Morang 500/330kV F2 Transformer | 1000 | 95.4 | 92.9 | 133.1599 | 1200 | 236.2 | 113.1 | 262 | S | 13 | 22 | Rowville 500/220kV A1 Transformer
| 330/220 kV | South Morang 330/220kV H1 Transformer | 700 | 550.7339 | 121.0204 | 563.8739 | 850 | 716.2072 | 99.1658 | 723 | S | 81 | 85 | South Morang 220kV - Thomastown 220kV 2
|  | South Morang 330/220kV H2 Transformer | 700 | 6.03e-06 | 0.00012016 | 0.00012031 | 850 | 6.1e-06 | 0.00012162 | 0 | S | 0 | 0
|  | South Morang 330/220kV H3 Transformer | 700 | 581.2714 | 76.0485 | 586.2251 | 1000 | 736.2233 | 83.1733 | 741 | S | 84 | 74 | South Morang 220kV - Thomastown 220kV 1
Regional Victoria | 220 kV | Red Cliffs 220kV - Buronga 220kV 1 | 437 | 33.3336 | 39.0605 | 51.3503 | 437 | 62.187 | 73.8501 | 97 | S | 12 | 22 | Red Cliffs 220kV - Buronga 220kV 2
|  | Horsham 220kV - Murra Warra 220kV 1 | 349 | 36.0503 | 36.2433 | 51.1195 | 360 | 64.0551 | 43.133 | 77 | D/W | 15 | 21 | Korangee 220kV - Wemen 220kV
|  | Kiamal 220kV - Murra Warra 220kV 1 | 393 | 38.4725 | 40.0197 | 55.5132 | 393 | 66.3195 | 45.3623 | 80 | D/W | 14 | 20 | Korangee 220kV - Wemen 220kV
|  | Carworp 220kV - Red Cliffs 220kV 1 | 393 | 68.8231 | 54.1567 | 87.5761 | 393 | 95.5563 | 46.2202 | 106 | D/W | 22 | 27 | Korangee 220kV - Wemen 220kV
|  | Kiamal 220kV - Carworp 220kV 1 | 393 | 52.0313 | 26.0684 | 58.1964 | 393 | 78.88 | 18.644 | 81 | D/W | 15 | 21 | Korangee 220kV - Wemen 220kV
|  | Red Cliffs 220kV - Wemen 220kV | 134 | 86.0151 | 7.2992 | 86.3242 | 134 | 142.7697 | 17.2598 | 144 | D/W | 64 | 107 | Kerang 220kV - Korangee 220kV
|  | Kerang 220kV - Korangee 220kV | 134 | 58.8532 | 23.2735 | 63.2879 | 134 | 115.8955 | 2.4018 | 116 | D/W | 47 | 87 | Korangee 220kV - Wemen 220kV
|  | Korangee 220kV - Wemen 220kV | 134 | 56.9607 | 22.1794 | 61.1265 | 134 | 115.8841 | 23.0128 | 118 | D/W | 46 | 88 | Kerang 220kV - Korangee 220kV
|  | Ballarat 220kV - Waubra 220kV | 393 | 13.1839 | 27.4554 | 30.4568 | 393 | 121.4809 | 49.7161 | 131 | D/W | 8 | 33 | Bulgana 220kV - Crowlands 220kV
|  | Ararat 220kV - Waubra 220kV | 393 | 13.4039 | 23.8458 | 27.3548 | 393 | 122.6526 | 41.9361 | 130 | D/W | 7 | 33 | Bulgana 220kV - Crowlands 220kV
|  | Ararat 220kV - Crowlands 220kV | 393 | 98.7657 | 32.1123 | 103.855 | 420 | 126.2785 | 35.9254 | 131 | D/W | 26 | 31 | Korangee 220kV - Wemen 220kV
|  | Bulgana 220kV - Horsham 220kV | 393 | 107.8843 | 29.6563 | 111.8862 | 421 | 135.1357 | 32.939 | 139 | D/W | 28 | 33 | Korangee 220kV - Wemen 220kV
|  | Bulgana 220kV - Crowlands 220kV | 393 | 109.0143 | 33.7529 | 114.12 | 427 | 136.4375 | 37.8125 | 142 | D/W | 29 | 33 | Korangee 220kV - Wemen 220kV
|  | Bendigo 220kV - Kerang 220kV | 264 | 14.8308 | 41.3082 | 43.8899 | 278 | 93.379 | 57.878 | 110 | D/W | 17 | 40 | Koorangee BESS unit
|  | Ballarat 220kV - Bendigo 220kV | 204 | 56.3221 | 20.7795 | 60.0331 | 232 | 242.8875 | 8.4252 | 243 | D/W | 29 | 105 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Ballarat 220kV - Berrybank 220kV | 383.5 | 53.4738 | 13.3281 | 55.1098 | 403 | 68.8603 | 19.0755 | 71 | D/W | 14 | 18 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Berrybank 220kV - Terang 220kV | 393 | 54.2415 | 30.2257 | 62.0946 | 432 | 69.9889 | 27.9795 | 75 | D/W | 16 | 17 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Ballarat 220kV - Moorabool 220kV 1 | 204 | 54.6925 | 6.9813 | 55.1363 | 204 | 107.4431 | 2.9685 | 107 | D/W | 27 | 52 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Ballarat 220kV - Moorabool 220kV 2 | 400 | 72.1933 | 6.2227 | 72.461 | 400 | 140.6629 | 13.5089 | 141 | D/W | 18 | 35 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Ballarat 220kV - Elaine 220kV | 391 | 92.8875 | 6.2659 | 93.0986 | 391 | 158.7848 | 3.5827 | 159 | D/W | 24 | 41 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Elaine 220kV - Moorabool 220kV | 391 | 58.4867 | 8.1475 | 59.0515 | 391 | 125.0754 | 18.5993 | 126 | D/W | 15 | 32 | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV
|  | Moorabool 220kV - Terang 220kV | 204 | 10.4282 | 14.8863 | 18.1755 | 237 | 60.8038 | 21.8667 | 65 | D/W | 9 | 27 | Berrybank 220kV - Terang 220kV
|  | Bendigo 220kV - Fosterville 220kV | 302 | 227.7572 | 37.1414 | 230.7658 | 302 | 319.6786 | 93.516 | 333 | D/W | 76 | 110 | Dederang 330kV - South Morang 330kV 2
|  | Fosterville 220kV - Shepparton 220kV | 302 | 253.1352 | 2.8389 | 253.1511 | 302 | 357.4941 | 11.3213 | 358 | D/W | 84 | 119 | Dederang 330kV - South Morang 330kV 2
|  | Glenrowan 220kV - Shepparton 220kV 1 | 393 | 141.8446 | 24.4078 | 143.9292 | 393 | 241.6202 | 41.2933 | 245 | D | 37 | 62 | Shepparton 220kV - Pine Lodge 220 kV
|  | Dederang 220kV - Goorambat East 220KV | 204 | 96.5322 | 0.90976 | 96.5365 | 204 | 126.9131 | 1.7491 | 127 | D | 47 | 62 | Dederang 330kV - South Morang 330kV 2
|  | Goorambat East 220KV - Shepparton 220kV | 204 | 93.9144 | 42.0352 | 102.8925 | 204 | 124.063 | 31.0154 | 128 | D | 50 | 63 | Dederang 330kV - South Morang 330kV 2
|  | Dederang 220kV - Glenrowan 220kV 1 | 393 | 112.8822 | 5.6597 | 113.024 | 393 | 188.0481 | 16.57 | 189 | D | 29 | 48 | Dederang 220kV - Glenrowan 220kV 2
|  | Dederang 220kV - Glenrowan 220kV 2 | 393 | 112.8822 | 5.6597 | 113.024 | 422 | 188.0481 | 16.57 | 189 | D | 29 | 45 | Dederang 220kV - Glenrowan 220kV 1
| 500/220 kV | Moorabool 500/220kV A1 Transformer | 1000 | 458.4197 | 84.7907 | 466.1954 | 1200 | 750.4415 | 138.8238 | 763 | S | 47 | 64 | Moorabool 500/220kV A2 Transformer
|  | Moorabool 500/220kV A2 Transformer | 1000 | 466.415 | 85.9926 | 474.276 | 1500 | 755.3188 | 139.438 | 768 | S | 47 | 51 | Moorabool 500/220kV A1 Transformer
* This is 5 minute short-term rating (N-1) available to the operator.
1 South Morang 330/220kV H2 Transformer is normally out of service under system normal conditions as it is used as a hot spare transformer.

## Maximum demand 2
Table 2 — Maximum demand snapshot: Interconnector power flow and limits
Interconnector | Interconnector target (MW)1 | Import Limit (MW)2 | Export Limit (MW)3 | Import constraint equation | Import Constraint description | Export constraint equation | Export Constraint description
Vic–NSW | 18 | 18 | 777 | V>>NIL_MLGT_MLGT | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Feedback | V>>N_X3_65_66 | Out= Balranald to Buronga (X3) 220kV line, avoid O/L Murray to Upper Tumut (65) 330kV line on trip of Murray to Lower Tumut (66) 330kV line, Feedback, Note: Darlington Pt -Wagga 132kV operated CLOSED
Vic–SA (Heywood) | 85 | 85 | 477 | V>>NIL_MLGT_MLGT | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Feedback | V>>X3_WERC_CWBUHO | Out = Balranald to Buronga (X3) 220 kV line, avoid O/L Wemen to Red Cliffs 220 kV line section on trip of Crowlands to Bulgana to Horsham 220 kV line (this trips Bulgana WF), feedback
Vic–SA (Murraylink) | 0 | 0 | 0 | V>>NIL_MLGT_MLGT | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Feedback | V^^SML_NSWRB_2 | Out = NSW Murraylink runback scheme, VIC to SA transfer limit on Murraylink to avoid voltage collapse at Red Cliffs for the loss of either the Darlington Point to Balranald (X5) or Balranald to Buronga (X3) 220kV lines
Tas–Vic (Basslink) | 172 | 172 | 425 | F_T++NIL_MG_R6 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | TVBL_ROC | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink
1 Note that actual interconnector power flows during a five-minute interval may deviate from their targets. Negative flows are in the import direction, whilst positive flows are in the export direction.
2 The import direction reflects southward flows on VNI and Basslink, and eastward flows on Heywood and Murraylink. Imports are reported as negative numbers, so that a positive import limit represents a forced export. This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 The export direction reflects northward flows on VNI and Basslink, and westward flows on Heywood and Murraylink. Exports are reported as positive numbers, so that a negative export limit represents a forced import.This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.

## High export to NSW 1
Table 3 — High export to NSW snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MW) | Continuous loading (N) (MVAr) | Continuous loading (N) (MVA) | Short–term rating* (N–1) (MVA) | Short-term loading (N-1) (MW) | Short-term loading (N-1) (MVAr) | Short-term loading (N-1) (MVA) | Rating type | (N) loading | (N–1) loading | Critical contingency
Northern Corridor | 330 kV | Dederang 330kV - Wodonga 330kV | 743 | 364.1505 | 94.7304 | 376.2704 | 743 | 478.3926 | 102.7179 | 489.2959 | D | 50.64% | 65.85% | Dederang 330kV - Murray 330kV 1
|  | Dederang 330kV - Murray 330kV 1 | 1185 | 417.082 | 0.88005 | 417.083 | 1303 | 706.6566 | 35.1948 | 707.5324 | D | 35.2% | 54.3% | Dederang 330kV - Murray 330kV 2
|  | Dederang 330kV - Murray 330kV 2 | 1185 | 413.3063 | 4.357 | 413.3293 | 1303 | 704.9175 | 29.8987 | 705.5513 | D | 34.88% | 54.15% | Dederang 330kV - Murray 330kV 1
|  | Dederang 330kV - South Morang 330kV 1 | 1145 | 493.8895 | 0.11094 | 493.8895 | 1343 | 834.236 | 148.2388 | 847.3042 | D | 43.13% | 63.09% | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330kV - South Morang 330kV 2 | 1145 | 492.5602 | 0.11383 | 492.5602 | 1343 | 833.524 | 148.4273 | 846.6363 | D | 43.02% | 63.04% | Dederang 330kV - South Morang 330kV 1
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 369 | 131.3326 | 19.8159 | 132.8191 | 369 | 237.7605 | 30.5776 | 239.7187 | D | 35.99% | 64.96% | Dederang 220kV - Mount Beauty 220kV 2
|  | Dederang 220kV - Mount Beauty 220kV 2 | 369 | 131.3326 | 19.8159 | 132.8191 | 369 | 237.7605 | 30.5776 | 239.7187 | D | 35.99% | 64.96% | Dederang 220kV - Mount Beauty 220kV 1
|  | Dartmouth 220kV - Mount Beauty 220kV | 230 | 157.0296 | 10.4796 | 157.3789 | 230 | 157.0297 | 11.6983 | 157.4648 | D | 68.43% | 68.46% | -
|  | Bogong 220kV - Mount Beauty 220kV | 1064 | 3.8098e-06 | 0.91942 | 0.91942 | 1064 | 0.0001641 | 0.9317 | 0.9317 | D | 0.08641% | 0.08757% | -
|  | Mount Beauty 220kV - West Kiewa 220kV | 97 | 4.2178e-06 | 0.44064 | 0.44064 | 97 | 1.7669e-05 | 0.44028 | 0.44028 | S | 0.4543% | 0.4539% | -
|  | Eildon 220kV - Thomastown 220kV | 738 | 69.3692 | 92.4673 | 115.5954 | 738 | 158.4338 | 91.8161 | 183.116 | D | 15.66% | 24.81% | Dederang 330kV - South Morang 330kV 1
|  | Eildon 220kV - Mount Beauty 220kV 1 | 356 | 60.2976 | 34.8344 | 69.6364 | 356 | 104.1856 | 36.2683 | 110.3179 | D | 19.56% | 30.99% | Dederang 330kV - South Morang 330kV 1
|  | Eildon 220kV - Mount Beauty 220kV 2 | 356 | 60.2976 | 34.8344 | 69.6364 | 356 | 104.1856 | 36.2683 | 110.3179 | D | 19.56% | 30.99% | Dederang 330kV - South Morang 330kV 1
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 90.8842 | 13.2458 | 91.8444 | 400 | 136.2352 | 20.6116 | 137.7856 | S | 27.01% | 34.45% | Dederang 330kV - South Morang 330kV 1
|  | Dederang 330/220kV H2 Transformer | 340 | 81.6561 | 11.4864 | 82.4601 | 400 | 121.1877 | 17.8904 | 122.5011 | S | 24.25% | 30.63% | Dederang 330kV - South Morang 330kV 1
|  | Dederang 330/220kV H3 Transformer | 240 | 77.346 | 6.8768 | 77.6511 | 240 | 115.9773 | 10.9465 | 116.4927 | S | 32.35% | 48.54% | Dederang 330kV - South Morang 330kV 1
| 500/330 kV | South Morang 500/330kV F1 Transformer | 1000 | 528.3255 | 55.9632 | 531.2812 | 1200 | 874.8708 | 99.7012 | 880.5336 | S | 53.13% | 73.38% | South Morang 500/330 kV F2 Transformer
Greater Melbourne and Geelong |  | South Morang 500/330kV F2 Transformer | 1000 | 533.4492 | 59.5559 | 536.7634 | 1200 | 877.4288 | 102.1244 | 883.352 | S | 53.68% | 73.61% | South Morang 500/330 kV F1 Transformer
| 330/220 kV | South Morang 330/220kV H1 Transformer1 | 700 | 39.131 | 35.0034 | 52.5021 | 850 | 92.3276 | 18.9818 | 94.2587 | S | 7.5% | 11.09% | Ringwood 220kV- Rowville 220kV
|  | South Morang 330/220kV H2 Transformer | 700 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | S | 0% | 0% | -
|  | South Morang 330/220kV H3 Transformer | 700 | 36.1485 | 2.9294 | 36.267 | 1000 | 78.5252 | 2.0269 | 78.5513 | S | 5.181% | 7.855% | Yallourn generating unit 4
* This is 5 minute short-term rating (N-1) available to the operator.
1 South Morang 330/220kV H2 Transformer is normally out of service under system normal conditions as it is used as a hot spare transformer.

## High export to NSW 2
Table 4 — High export to NSW snapshot: Interconnector power flow and limits
Interconnector | Interconnector target (MW)1 | Import Limit (MW)2 | Export Limit (MW)3 | Import constraint equation | Import Constraint description | Export constraint equation | Export Constraint description
Vic–NSW | 1476 | -627 | 1476 | N^^V_NIL_ARWBBA | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | V>>N_NIL_65_66 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback
Vic–SA (Heywood) | -483 | -674 | -278 | SV_550_TEST | Out = Nil, SA to Vic on Heywood limit of 550 MW, limit for testing of Heywood interconnection upgrade | V::N_NIL_V1 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV.
Vic–SA (Murraylink) | -54 | -125 | -54 | SVML_ROC_80 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | V>>N_NIL_65_66 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback
Tas–Vic (Basslink) | -459 | -459 | -265 | F_T++NIL_MG_R6 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | TVBL_ROC | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink
1 Note that actual interconnector power flows during a five-minute interval may deviate from their targets. Negative flows are in the import direction, whilst positive flows are in the export direction.
2 The import direction reflects southward flows on VNI and Basslink, and eastward flows on Heywood and Murraylink. Imports are reported as negative numbers, so that a positive import limit represents a forced export. This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 The export direction reflects northward flows on VNI and Basslink, and westward flows on Heywood and Murraylink. Exports are reported as positive numbers, so that a negative export limit represents a forced import.This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.

## High Wind 1
Table 1 — Maximum demand snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MW) | Continuous loading (N) MVAr | MVA | Short–term rating* (N–1) (MVA) | Short-term loading (N-1) (MW) | MVAr | MVA | Rating type | (N) loading | (N–1) loading | Critical contingency
South–West Corridor | 500 kV | Heywood 500kV - Tarrone 500kV | 2771 | 364.8644 | 170.7547 | 402.8439 | 2771 | 584.4342 | 98.9257 | 593 | S | 15 | 21 | Tarrone 500kV - Mortlake 500 kV
|  | Haunted Gully 500kV - cressy 500kV | 3248 | 605.6282 | 83.3331 | 611.3346 | 3248 | 1375.7158 | 12.0451 | 1376 | S | 19 | 42 | Cressy 500kV - Mortlake 500kV
|  | Cressy 500kV - Moorabool 500kV 1 | 3248 | 789.6643 | -67.6666 | 792.5582 | 3248 | 1999.3624 | -58.169 | 2000 | S | 24 | 62 | Cressy 500kV - Moorabool 500kV 2
|  | Cressy 500kV - Moorabool 500kV 2 | 3248 | 765.7569 | -67.1744 | 768.6976 | 3248 | 1980.8378 | -87.7777 | 1983 | S | 24 | 61 | Cressy 500kV - Moorabool 500kV 1
|  | Cressy 500kV - Mortlake 500kV | 2598 | 329.5139 | 99.5326 | 344.2182 | 2598 | 1370.8704 | 12.0893 | 1371 | S | 13 | 53 | Haunted Gully 500kV - cressy 500kV
|  | Heywood 500kV - Mortlake 500kV | 2771 | 91.4725 | 183.4803 | 205.0176 | 2771 | 122.7183 | 240.7846 | 270 | S | 7 | 10 | Tarrone 500kV - Mortlake 500 kV
|  | Alcoa Portland 500kV - Heywood 500kV 1 | 1386 | 198.4713 | 209.5711 | 288.6363 | 1386 | 395.7245 | 312.5527 | 504 | S | 21 | 36 | Alcoa Portland 500kV - Heywood 500kV 2
|  | Alcoa Portland 500kV - Heywood 500kV 2 | 1386 | 197.2764 | 208.3753 | 286.9464 | 1386 | 395.7241 | 312.5016 | 504 | S | 21 | 36 | Alcoa Portland 500kV - Heywood 500kV 1
Regional Victoria | 220 kV | Red Cliffs 220kV - Buronga 220kV 1 | 457 | 33.3336 | 39.0605 | 51.3503 | 457 | 62.187 | 73.8501 | 97 | S | 11 | 21 | red cliff to Buronga Line 2 off
|  | Horsham 220kV - Murra Warra 220kV 1 | 505 | 80.7332 | 9.8641 | 81.3336 | 543.5 | 343.0669 | 32.6101 | 345 | D/W | 16 | 63 | Red Cliffs 220kV-Kiamal 220 kV
|  | Kiamal 220kV - Murra Warra 220kV 1 | 566 | 262.2058 | 14.3905 | 262.6004 | 566 | 469.995 | 25.6542 | 471 | D/W | 46 | 83 | Ararat 220 kV-Crowlands 220 KV
|  | Red Cliffs 220kV - Wemen 220kV | 452 | 95.6608 | 74.1044 | 121.006 | 487 | 197.6157 | 80.229 | 213 | D/W | 27 | 44 | Bendigo 220kV-Ballarat 220kV
|  | Kerang 220kV - Korangee 220kV | 452 | 60.5023 | 33.8885 | 69.3466 | 485 | 153.1739 | 72.1209 | 169 | D/W | 15 | 35 | Bendigo 220kV-Ballarat 220kV
|  | Korangee 220kV - Wemen 220kV | 452 | 82.0684 | 53.5738 | 98.007 | 485 | 181.1128 | 72.2163 | 195 | D/W | 22 | 40 | Bendigo 220kV-Ballarat 220kV
|  | Ararat 220kV - Crowlands 220kV | 566 | 241.064 | 61.4035 | 248.7614 | 660 | 469.8334 | 95.1969 | 479 | D/W | 44 | 73 | Murra Wurra 220 Kv-Kiamal 220 kV
|  | Bulgana 220kV - Horsham 220kV | 566 | 58.2013 | 8.0418 | 58.7542 | 616.5 | 300.2004 | 31.5834 | 302 | D/W | 10 | 49 | Murra Wurra 220 Kv-Kiamal 220 kV
|  | Bulgana 220kV - Crowlands 220kV | 566 | 165.9501 | 57.3237 | 175.5718 | 664 | 165.9501 | 57.3237 | 176 | D/W | 31 | 27 | Murra Wurra 220 Kv-Kiamal 220 kV
|  | Bendigo 220kV - Kerang 220kV | 497 | 22.4789 | 16.4269 | 27.8414 | 545 | 114.7487 | 53.9802 | 127 | D/W | 6 | 23 | Bendigo 220kV-Ballarat 220kV
|  | Ballarat 220kV - Bendigo 220kV | 390 | 302.7972 | 96.443 | 317.7852 | 421 | 366.7337 | 135.453 | 391 | D/W | 81 | 93 | Murra Wurra 220 Kv-Kiamal 220 kV
|  | Ballarat 220kV - Berrybank 220kV | 522.5 | -242.786 | 6.7615 | 242.8802 | 555.5 | -397.3155 | 23.1753 | 398 | D/W | 46 | 72 | Moorabool 220kV - Terang 220kV
|  | Berrybank 220kV - Terang 220kV | 519.5 | 21.0664 | 5.7295 | 21.8316 | 552.5 | 262.9514 | 0.71667 | 263 | D/W | 4 | 48 | Berrybank 220kV-Ballarat 220kV
|  | Ballarat 220kV - Moorabool 220kV 1 | 390 | 203.3212 | 40.6964 | 207.3541 | 390 | 330.0839 | 107.085 | 347 | D/W | 53 | 89 | Elaine 220kV - Moorabool 220kV
|  | Ballarat 220kV - Moorabool 220kV 2 | 591 | 262.6487 | 71.4593 | 272.1962 | 591 | 421.6118 | 169.7128 | 454 | D/W | 46 | 77 | Elaine 220kV - Moorabool 220kV
|  | Ballarat 220kV - Elaine 220kV | 566 | 47.422 | 2.6749 | 47.4974 | 566 | 454.7108 | 72.2733 | 460 | D/W | 8 | 81 | Elaine 220kV - Moorabool 220kV
|  | Elaine 220kV - Moorabool 220kV | 566 | 406.9344 | 96.3399 | 418.183 | 566 | 503.2501 | 183.5753 | 536 | D/W | 74 | 95 | Ballarat 220kV - Moorabool 220kV 2
|  | Moorabool 220kV - Terang 220kV | 390 | 167.1038 | 15.5609 | 167.8268 | 452 | 357.5599 | 143.7465 | 385 | D/W | 43 | 85 | Berrybank 220kV-Ballarat 220kV
|  | Bendigo 220kV - Fosterville 220kV | 439 | 182.2098 | 57.6659 | 191.1171 | 439 | 182.2098 | 57.6659 | 191 | D/W | 44 | 44 | Mortlake 500 KV-Cressy 500 KV
|  | Fosterville 220kV - Shepparton 220kV | 439 | 165.5986 | 61.0028 | 176.4773 | 439 | 531.5 | 59.9 | 535 | D/W | 40 | 122 | Mortlake 500 KV-Cressy 500 KV
|  | Glenrowan 220kV - Shepparton 220kV 1 | 461 | 2.4002 | 32.8655 | 32.9531 | 461 | 78.1953 | 5.2417 | 78 | D | 7 | 17 | Bendigo 220kV-Ballarat 220kV
|  | Dederang 220kV - Glenrowan 220kV 1 | 564 | 36.2588 | 12.8154 | 38.4569 | 564 | 112.1846 | 22.682 | 114 | D | 7 | 20 | Bendigo 220kV-Ballarat 220kV
|  | Dederang 220kV - Glenrowan 220kV 2 | 566 | 36.2588 | 12.8154 | 38.4569 | 607 | 112.1846 | 22.682 | 114 | D | 7 | 19 | Bendigo 220kV-Ballarat 220kV
* This is 5 minute short-term rating (N-1) available to the operator.

## High Wind 2
Table 4 — High export to NSW snapshot: Interconnector power flow and limits
Interconnector | Interconnector target (MW)1 | Import Limit (MW)2 | Export Limit (MW)3 | Import constraint equation | Import Constraint description | Export constraint equation | Export Constraint description
Vic–NSW | 888 | 564.86 | 884.96 | V>>NIL_MLGT_MLGT_R2 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Feedback | V^^N_CNYS_1 | Out = Canberra to Yass (9), avoid voltage collapse around Murray for loss of all APD potlines
Vic–SA (Heywood) | 126 | 32.12 | 378.92 | V>>NIL_SMTX_SMTX_R2 | Out= Nil, avoid O/L the remaining South Morang 500/330kV F transformer on trip of one South Morang 500/330kV F transformer, radial mode, Yallourn W1 on 220kV mode, Feedback | V>>NIL_BABE_HOMRKM | Out= Nil, avoid O/L Ballarat to Bendigo 220kV line on trip of Horsham to Murra Warra to Kiamal 220kV line (this trips Murra Warra WF), Feedback
Vic–SA (Murraylink) | 0 | 0 | 0 | SVML_ZERO | SA to Vic on ML upper transfer limit of 0 MW | SVML_ZERO | Vic to SA on ML upper transfer limit of 0 MW
Tas–Vic (Basslink) | -28.9 | -250.6 | -28.9 | VTBL_ROC | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | F_MAIN++NIL_MG_R6 | Out = Nil, Raise 6 sec requirement for a Mainland Generation Event, Basslink able transfer FCAS
1 Note that actual interconnector power flows during a five-minute interval may deviate from their targets. Negative flows are in the import direction, whilst positive flows are in the export direction.
2 The import direction reflects southward flows on VNI and Basslink, and eastward flows on Heywood and Murraylink. Imports are reported as negative numbers, so that a positive import limit represents a forced export. This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 The export direction reflects northward flows on VNI and Basslink, and westward flows on Heywood and Murraylink. Exports are reported as positive numbers, so that a negative export limit represents a forced import.This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.