## User guide
System strength effectiveness factors - Minimum Fault Level
To support procurement of services identified under the Victorian System Strength Requirement RIT-T, AEMO Victorian Planning (AVP) has developed system strength effectiveness factors to indicate how prospective solutions connecting to the Declared Shared Network (DSN) contribute to the minimum fault level at each of the system strength nodes in Victoria (Dederang 220 kV, Hazelwood 500 kV, Moorabool 220 kV, Red Cliffs 220 kV, and Thomastown 220 kV). For the purpose of this study, a synchronous condenser (syncon) with a 500 MVA fault level contribution is connected sequentially to all DSN terminal station 132kV, 220kV, 330kV and 500kV busbars within the intact network. Fault levels are then calculated using the method described in Appendix 4 of the 2020 System Strength and Inertia Report, consistent with the RIT-T methodology. The increase in minimum fault level at each system strength node, that is the difference between the fault level at the system strength node with and without the syncon in service, is then recorded. The effectiveness factor is calculated as the ratio of the increase in minimum fault level at the system strength node to the syncon contribution of 500 MVA.
Key assumptions
Combination VIC_8 from the Victorian System Strength Requirements, within the Victorian Transfer Limit Advice – System Normal, has been selected for the dispatch combination in this study. The synchronous units in this combination meet the minimum three-phase fault levels at the five system strength nodes in the Victorian Declared Shared Network (DSN) and are relatively geographically spread across Victoria. The VIC_8 combination does not include any Yallourn units, thereby removing any impact related to the forthcoming retirement. • The timings for major network augmentation projects (PEC Stage 2, HumeLink, WRL and VNI West) are based on the July 2025 NEM Transmission Augmentation Information. Projects are included in the first financial year following the "In Service Date". When considering system strength, it is the in service date that is relevant rather than the full capacity available date. • The network operating mode in this study is the R6 mode, which is in place for the majority of time. Different operating modes may yield different results, particularly for connections to the network south- east of Melbourne. • Consistent with the approach in the Victorian System Strength Requirement RIT-T, interstate fault level contributions will be limited to the amount required for neighbouring regions to meet their own minimum fault level requirements, plus PEC syncons. • The Ararat syncon has been included as a source of synchronous fault current in the calculation, as a contract has already been established with Ararat syncon to provide system strength.
Results
Results are shown in worksheet "Effectiveness Factors". For each terminal station on the Victorian DSN, the effectiveness factors with an intact system have been provided to each of the system strength nodes. This includes buses where the network topology means that the effectiveness factors are different but otherwise assumes that the connection is to the terminal station bus. Proponents considering connections outside of terminal stations, or to downstream networks, should account for the impedance of the network to the nearest DSN substation. The effectiveness factors are heavily impacted by the geographical location. For instance, in the financial year 2027, deploying a solution with a 500 MVA fault level at the Geelong 220 kV bus may have 94% effectiveness factor at Moorabool node but only 1% at Red Cliffs node. Changes to the surrounding network, such as augmentations and operating modes, can also influence the effectiveness factors from year to year. This is particularly evident where the background fault level increases has the effect of reducing the effectiveness factor to surrounding nodes due to the non-linear characteristics of system strength.
Efficient level
This study has focused on calculating the effectiveness factors for contribution of synchronous machines to minimum fault levels in the Victorian DSN. The efficient level is significantly influenced by the forecast location and quantum of grid-following Inverter-Based Resources (IBR), such as wind and solar generation, that demand system strength. While the same principle applies to the efficient level, the locations where solutions for the efficient level are most efficient will be closer to the IBR requiring remediation rather than the system strength nodes. AVP expects to provide the effectiveness factors for efficient level requirements in future, once a number of changes including the 2025 IBR forecast, are incorporated into the modelling.

## Effectiveness Factors
Terminal Station | Voltage (kV) | Dederang (FY27) | Hazelwood (FY27) | Moorabool (FY27) | Red Cliffs (FY27) | Thomastown (FY27) | Dederang (FY28) | Hazelwood (FY28) | Moorabool (FY28) | Red Cliffs (FY28) | Thomastown (FY28) | Dederang (FY29) | Hazelwood (FY29) | Moorabool (FY29) | Red Cliffs (FY29) | Thomastown (FY29) | Dederang (FY30) | Hazelwood (FY30) | Moorabool (FY30) | Red Cliffs (FY30) | Thomastown (FY30) | Dederang (FY31) | Hazelwood (FY31) | Moorabool (FY31) | Red Cliffs (FY31) | Thomastown (FY31) | Dederang (FY32) | Hazelwood (FY32) | Moorabool (FY32) | Red Cliffs (FY32) | Thomastown (FY32)
ALTONA | 220 | 12.4% | 53% | 48.1% | 0.9% | 42.6% | 12.2% | 52.1% | 47.6% | 1.3% | 42.2% | 11.5% | 54% | 46.7% | 1.1% | 41.9% | 11.5% | 54% | 46.7% | 1.1% | 41.9% | 11.1% | 53% | 46% | 1.4% | 41.2% | 10.4% | 48.9% | 44.3% | 1.9% | 38.9%
ARARAT | 220 | 4.7% | 14.3% | 24.9% | 3.6% | 9.8% | 4.8% | 14.2% | 24.7% | 4% | 9.7% | 4.5% | 14.3% | 24.4% | 3.9% | 9.4% | 4.5% | 14.3% | 24.4% | 3.9% | 9.4% | 7.4% | 32.8% | 32.1% | 2% | 20.4% | 7.1% | 25.5% | 26.9% | 2.8% | 15.9%
BALLARAT | 220 | 11.8% | 39.1% | 71.9% | 2.3% | 26.6% | 11.8% | 38.5% | 71.8% | 2.9% | 26.3% | 11.2% | 39.3% | 71.4% | 2.6% | 25.9% | 11.2% | 39.3% | 71.4% | 2.6% | 25.9% | 11.8% | 44.8% | 73.4% | 2.4% | 29.1% | 11% | 40.5% | 71.6% | 2.5% | 26%
BENDIGO | 220 | 23.1% | 26.5% | 34.6% | 7.2% | 19.1% | 23.6% | 25.7% | 33.8% | 8.3% | 18.6% | 22.9% | 25.3% | 32.5% | 7.9% | 17.6% | 22.9% | 25.3% | 32.5% | 7.9% | 17.6% | 23.5% | 28.2% | 33.2% | 7.8% | 19.3% | 20.2% | 31.2% | 33.2% | 3.4% | 20.1%
BERRYBANK | 220 | 10.6% | 36.9% | 68.4% | 1.8% | 25% | 10.6% | 36.4% | 68.3% | 2.4% | 24.7% | 10.1% | 37.1% | 68% | 2.1% | 24.4% | 10.1% | 37.1% | 68% | 2.1% | 24.4% | 10.5% | 41.3% | 69.5% | 2.1% | 26.8% | 9.8% | 37.3% | 68.1% | 2.2% | 24%
BOGONG | 220 | 76% | 33.8% | 21.3% | 1.1% | 28.2% | 76% | 31.5% | 20% | 2% | 26.4% | 75.7% | 30.9% | 18.1% | 1.6% | 24.5% | 75.7% | 30.8% | 18.1% | 1.6% | 24.5% | 75.5% | 30.6% | 17.8% | 1.9% | 24.3% | 76.8% | 33.5% | 18.6% | 1.9% | 22.7%
BROOKLYN | 220 | 12.5% | 52.8% | 46.8% | 0.9% | 43.8% | 12.2% | 52% | 46.3% | 1.3% | 43.3% | 11.6% | 53.9% | 45.4% | 1.1% | 43.1% | 11.6% | 53.9% | 45.4% | 1.1% | 43% | 11.1% | 52.9% | 44.6% | 1.4% | 42.3% | 10.4% | 48.9% | 43% | 1.9% | 40.1%
BRUNSWICK | 220 | 15% | 60.1% | 31.7% | 0.7% | 55.5% | 14.7% | 59% | 31.1% | 1.2% | 54.9% | 13.6% | 63.1% | 29.4% | 1% | 52.9% | 13.6% | 63.1% | 29.4% | 1% | 52.9% | 13% | 61.8% | 28.6% | 1.3% | 52% | 12.1% | 59.1% | 27.4% | 1.7% | 51.5%
BULGANA | 500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 10.2% | 50.3% | 36.4% | 2.1% | 30.7% | 10.2% | 36.2% | 27% | 3.9% | 22.1%
BULGANA | 220 | 4.5% | 13.2% | 22.5% | 5.6% | 9% | 4.7% | 13.1% | 22.3% | 6.1% | 9% | 4.3% | 13.1% | 21.8% | 5.9% | 8.7% | 4.3% | 13.1% | 21.8% | 5.9% | 8.7% | 9.1% | 42.5% | 33.8% | 2.7% | 26.1% | 8.9% | 31.5% | 26.3% | 4.2% | 19.4%
BURONGA | 330 | 3.2% | 5.1% | 5.9% | 49.7% | 3.6% | 5.1% | 5.9% | 5.6% | 34.8% | 4.3% | 4% | 5% | 4.7% | 33.4% | 3.5% | 4.1% | 5% | 4.7% | 33.4% | 3.5% | 4.3% | 6.2% | 5% | 33.6% | 4.2% | 4.1% | 9.6% | 7.4% | 33.2% | 6%
BURONGA | 220 | 4.4% | 6.6% | 7.7% | 79.1% | 4.7% | 6% | 7.1% | 7.3% | 73% | 5.2% | 4.9% | 6.2% | 6.2% | 72.2% | 4.3% | 4.9% | 6.2% | 6.2% | 72.2% | 4.3% | 5.4% | 8.2% | 6.8% | 72.3% | 5.5% | 4.8% | 11.5% | 8.8% | 72.1% | 7.2%
CRANBOURNE | 500 | 11.6% | 76.2% | 29.9% | 0.7% | 37.2% | 11.4% | 75.6% | 29.4% | 1.1% | 36.7% | 10.9% | 77.9% | 28.8% | 0.9% | 37% | 10.9% | 77.8% | 28.8% | 0.9% | 37% | 10.3% | 76.6% | 27.9% | 1.2% | 35.8% | 10.3% | 74.2% | 26% | 1.6% | 32.9%
CRANBOURNE | 220 | 12.9% | 66.7% | 30.4% | 0.7% | 44.8% | 12.6% | 65.9% | 29.9% | 1.1% | 44.3% | 11.7% | 70.4% | 28.3% | 0.9% | 42.4% | 11.7% | 70.4% | 28.3% | 0.9% | 42.4% | 11.1% | 69.2% | 27.6% | 1.2% | 41.4% | 11.7% | 67% | 25.6% | 1.6% | 37.3%
CRESSY | 500 | 12.2% | 55.4% | 51.2% | 1.1% | 35.2% | 12.1% | 54.6% | 50.8% | 1.6% | 34.8% | 11.5% | 56% | 50.1% | 1.4% | 34.7% | 11.5% | 56% | 50.1% | 1.4% | 34.7% | 11% | 54.4% | 49.1% | 1.7% | 33.5% | 10.5% | 49.6% | 46.7% | 2.3% | 30.2%
CRESSY | 220 | 11.7% | 52.9% | 48.9% | 1% | 33.7% | 11.6% | 52.2% | 48.5% | 1.5% | 33.2% | 11% | 53.5% | 47.8% | 1.3% | 33.1% | 11% | 53.5% | 47.8% | 1.3% | 33.1% | 10.5% | 52% | 46.9% | 1.6% | 32% | 10.1% | 47.4% | 44.6% | 2.2% | 28.9%
CROWLANDS | 220 | 4.6% | 13.9% | 24% | 4.3% | 9.5% | 4.8% | 13.8% | 23.8% | 4.7% | 9.4% | 4.4% | 13.8% | 23.4% | 4.5% | 9.1% | 4.4% | 13.8% | 23.4% | 4.5% | 9.1% | 7.9% | 35.8% | 32.6% | 2.2% | 22.2% | 7.7% | 27.4% | 26.5% | 3.3% | 17%
DARTMOUTH | 220 | 67.7% | 30.3% | 19.1% | 1% | 25.2% | 67.6% | 28.2% | 17.9% | 1.8% | 23.6% | 67.3% | 27.6% | 16.2% | 1.5% | 21.9% | 67.3% | 27.6% | 16.2% | 1.5% | 21.9% | 67.2% | 27.4% | 15.9% | 1.7% | 21.7% | 68.4% | 30% | 16.6% | 1.7% | 20.3%
DEDERANG | 330 | 49.3% | 33.4% | 20.6% | 1.1% | 26.2% | 47.1% | 30.5% | 19.1% | 2.3% | 24% | 44.8% | 29% | 16.9% | 1.7% | 21.8% | 44.8% | 28.9% | 16.8% | 1.8% | 21.8% | 44.5% | 28.6% | 16.5% | 2% | 21.5% | 44.6% | 32.2% | 18.6% | 2.2% | 22.7%
DEDERANG | 220 | 99.6% | 33.8% | 21.8% | 1.3% | 27.1% | 99.6% | 31.2% | 20.3% | 2.4% | 25.1% | 99.6% | 30% | 18.3% | 1.9% | 23% | 99.6% | 30% | 18.2% | 1.9% | 23% | 99.7% | 29.9% | 17.9% | 2.2% | 22.9% | 99.7% | 33.2% | 19.5% | 2.2% | 23%
DEER PARK | 220 | 12.2% | 52.4% | 56.8% | 1% | 38.9% | 12% | 51.6% | 56.4% | 1.4% | 38.4% | 11.4% | 53.2% | 55.7% | 1.2% | 38.2% | 11.4% | 53.2% | 55.7% | 1.2% | 38.2% | 11% | 52.5% | 55% | 1.5% | 37.7% | 10.4% | 48.3% | 53.4% | 2% | 35%
DRIFFIELD | 500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7.9% | 98.9% | 21.4% | 0.9% | 27.1% | 7.8% | 98.8% | 20% | 1.2% | 24.9%
EAST ROWVILLE | 220 | 13.6% | 65.1% | 31.1% | 0.7% | 48.2% | 13.3% | 64.2% | 30.6% | 1.1% | 47.7% | 12.2% | 69.5% | 28.8% | 0.9% | 45.1% | 12.1% | 69.5% | 28.7% | 0.9% | 45% | 11.6% | 68.3% | 28% | 1.2% | 44% | 12.4% | 66.1% | 26% | 1.6% | 39.5%
EILDON | 220 | 33.1% | 44.2% | 25.7% | 0.9% | 41.7% | 32.9% | 42.6% | 24.8% | 1.5% | 40.6% | 31.9% | 44% | 23.1% | 1.2% | 38.8% | 31.9% | 43.9% | 23.1% | 1.2% | 38.8% | 31.4% | 43.2% | 22.6% | 1.4% | 38.3% | 35.1% | 44.6% | 20.5% | 1.7% | 28.3%
ELAINE | 220 | 11.7% | 41.6% | 78.1% | 1.9% | 28.2% | 11.6% | 41% | 78% | 2.4% | 27.8% | 11% | 41.8% | 77.8% | 2.2% | 27.5% | 11% | 41.8% | 77.8% | 2.2% | 27.5% | 11.6% | 46.8% | 80.7% | 2.2% | 30.4% | 10.8% | 42.3% | 79.4% | 2.4% | 27.3%
FISHERMANS BEND | 220 | 12.7% | 50.5% | 33.1% | 0.7% | 56.7% | 12.4% | 49.6% | 32.5% | 1.1% | 56.4% | 11.6% | 52.1% | 31.3% | 0.9% | 55.8% | 11.6% | 52.1% | 31.3% | 0.9% | 55.8% | 11.2% | 50.9% | 30.6% | 1.2% | 55.2% | 10.1% | 47.8% | 29.4% | 1.6% | 54.8%
FOSTERVILLE | 220 | 29.1% | 26.4% | 31.3% | 5.8% | 19.4% | 29.6% | 25.4% | 30.4% | 7% | 18.7% | 28.9% | 24.9% | 29% | 6.5% | 17.6% | 28.9% | 24.9% | 29% | 6.5% | 17.6% | 29.5% | 27.3% | 29.5% | 6.5% | 19% | 26.3% | 30% | 29.5% | 3% | 19.6%
GEELONG | 220 | 12.4% | 51% | 93.5% | 1.3% | 34.8% | 12.3% | 50.2% | 93.5% | 1.8% | 34.3% | 11.6% | 51.5% | 93.3% | 1.6% | 34.1% | 11.6% | 51.5% | 93.3% | 1.6% | 34.1% | 11.4% | 52.3% | 93.2% | 1.8% | 34.4% | 10.8% | 47.7% | 93% | 2.2% | 31.3%
GIFFARD (GIPPSLAND) | 500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 7.3% | 94% | 19.9% | 0.8% | 25.2% | 7.3% | 94% | 18.6% | 1.2% | 23.2%
GLENROWAN | 220 | 79.3% | 31% | 22.3% | 1.8% | 24.5% | 79.4% | 28.8% | 20.9% | 2.9% | 22.8% | 79.2% | 27.8% | 19% | 2.4% | 21% | 79.2% | 27.8% | 19% | 2.4% | 21% | 79.4% | 28.1% | 18.8% | 2.6% | 21.1% | 78.3% | 31% | 20% | 2.2% | 21.2%
GNARWARRE | 220 | 11.7% | 47.1% | 91.6% | 1.3% | 31.7% | 11.6% | 46.3% | 91.6% | 1.8% | 31.3% | 11% | 47.5% | 91.5% | 1.6% | 31.1% | 11% | 47.5% | 91.5% | 1.6% | 31.1% | 10.9% | 48.8% | 91.7% | 1.8% | 31.7% | 10.3% | 44.4% | 91.5% | 2.2% | 28.7%
GOLDEN PLAINS | 220 | 11.7% | 52.9% | 48.9% | 1% | 33.6% | 11.6% | 52.1% | 48.5% | 1.5% | 33.2% | 11% | 53.5% | 47.8% | 1.3% | 33.1% | 11% | 53.5% | 47.8% | 1.3% | 33.1% | 10.5% | 52% | 46.9% | 1.6% | 32% | 10.1% | 47.3% | 44.5% | 2.2% | 28.9%
GOORAMBAT EAST | 220 | 70% | 28.4% | 21% | 1.8% | 22.4% | 70.1% | 26.4% | 19.8% | 2.8% | 20.9% | 69.9% | 25.5% | 18% | 2.4% | 19.2% | 69.9% | 25.5% | 18% | 2.4% | 19.2% | 70.1% | 25.9% | 17.9% | 2.6% | 19.4% | 68.8% | 28.6% | 18.9% | 2.1% | 19.5%
HAUNTED GULLY | 500 | 11.8% | 53.3% | 49.3% | 1.1% | 33.9% | 11.7% | 52.6% | 48.9% | 1.6% | 33.5% | 11.1% | 53.9% | 48.2% | 1.4% | 33.4% | 11.1% | 53.9% | 48.2% | 1.4% | 33.4% | 10.6% | 52.4% | 47.3% | 1.7% | 32.3% | 10.2% | 47.8% | 45% | 2.3% | 29.2%
HAZELWOOD | 500 | 8.3% | 99.9% | 21.7% | 0.5% | 25.5% | 8.1% | 99.9% | 21.4% | 0.8% | 25.2% | 8.2% | 99.9% | 21.8% | 0.7% | 27.7% | 8.2% | 99.9% | 21.8% | 0.7% | 27.7% | 7.8% | 99.9% | 21.2% | 0.9% | 26.8% | 7.7% | 99.9% | 19.7% | 1.2% | 24.6%
HAZELWOOD BUS 1-4 | 220 | 7.1% | 85.6% | 18.7% | 0.4% | 22% | 7% | 85.6% | 18.4% | 0.7% | 21.7% | 6.2% | 74.3% | 16.4% | 0.5% | 20.8% | 6.2% | 74.3% | 16.4% | 0.5% | 20.7% | 5.9% | 74.3% | 15.9% | 0.7% | 20.1% | 5.8% | 74.3% | 14.8% | 0.9% | 18.5%
HAZELWOOD BUS 5-6 | 220 | 12.7% | 59.5% | 29.1% | 0.7% | 49.3% | 12.5% | 58.7% | 28.6% | 1.1% | 48.9% | 9.8% | 82% | 24.5% | 0.8% | 36.7% | 9.8% | 82% | 24.5% | 0.8% | 36.7% | 9.3% | 81.3% | 23.8% | 1% | 35.7% | 9.4% | 80.1% | 22.2% | 1.4% | 33.1%
HEATHERTON | 220 | 13.4% | 61.3% | 30.7% | 0.7% | 58% | 13.1% | 60.3% | 30.1% | 1.1% | 57.5% | 11.9% | 66% | 28.2% | 0.9% | 54.4% | 11.9% | 65.9% | 28.2% | 0.9% | 54.4% | 11.3% | 64.7% | 27.4% | 1.2% | 53.5% | 10.9% | 62.2% | 26% | 1.6% | 51.7%
HEYWOOD | 500 | 10.6% | 47.3% | 43.7% | 1.1% | 30.1% | 10.6% | 46.7% | 43.3% | 1.7% | 29.8% | 10% | 47.8% | 42.7% | 1.5% | 29.6% | 10% | 47.8% | 42.7% | 1.5% | 29.6% | 9.6% | 46.5% | 41.9% | 1.8% | 28.7% | 9.2% | 42.6% | 40% | 2.4% | 26%
HEYWOOD | 275 | 9.5% | 42.2% | 39% | 1.2% | 26.9% | 9.6% | 41.7% | 38.7% | 1.8% | 26.7% | 9.1% | 42.7% | 38.1% | 1.6% | 26.5% | 9.1% | 42.7% | 38% | 1.6% | 26.5% | 8.7% | 41.6% | 37.4% | 1.9% | 25.7% | 8.3% | 38.3% | 35.8% | 2.4% | 23.4%
HORSHAM | 220 | 4.2% | 11% | 17.8% | 12.9% | 7.6% | 4.6% | 11% | 17.5% | 13.4% | 7.6% | 4.2% | 10.8% | 16.9% | 13.2% | 7.2% | 4.2% | 10.8% | 16.9% | 13.2% | 7.2% | 7.4% | 29.5% | 24.1% | 9.4% | 18.3% | 7% | 23.6% | 19.8% | 11.5% | 14.6%
JEERALANG | 220 | 7.1% | 84.6% | 18.5% | 0.4% | 21.7% | 6.9% | 84.6% | 18.2% | 0.6% | 21.4% | 6.1% | 73.1% | 16.1% | 0.5% | 20.4% | 6.1% | 73.1% | 16.1% | 0.5% | 20.4% | 5.8% | 73.1% | 15.6% | 0.7% | 19.7% | 5.7% | 73.1% | 14.6% | 0.9% | 18.2%
KEILOR | 500 | 13.4% | 63% | 41.5% | 0.9% | 40% | 13.1% | 62.1% | 40.9% | 1.3% | 39.5% | 12.5% | 63.8% | 40.1% | 1.1% | 39.4% | 12.5% | 63.8% | 40% | 1.1% | 39.4% | 11.8% | 61.2% | 38.9% | 1.5% | 37.7% | 11.4% | 56.2% | 36.1% | 2.1% | 34.3%
KEILOR BUS 1-3 | 220 | 12.7% | 54.7% | 52.2% | 0.9% | 41.3% | 12.4% | 53.8% | 51.8% | 1.4% | 40.8% | 11.8% | 55.6% | 50.9% | 1.2% | 40.6% | 11.8% | 55.6% | 50.9% | 1.2% | 40.6% | 11.3% | 54.6% | 50.1% | 1.5% | 39.8% | 10.7% | 50.2% | 48.3% | 2% | 37.2%
KEILOR BUS 2 | 220 | 14.1% | 55.2% | 33.3% | 0.8% | 66.8% | 13.8% | 54.3% | 32.7% | 1.2% | 66.5% | 12.9% | 57.2% | 31.3% | 1% | 65.7% | 12.9% | 57.2% | 31.3% | 1% | 65.7% | 12.4% | 55.9% | 30.5% | 1.3% | 65.1% | 11.1% | 52.7% | 29.3% | 1.7% | 65.3%
KERANG | 220 | 13.4% | 16.3% | 20.9% | 21.5% | 11.7% | 14.5% | 16.1% | 20.2% | 22.7% | 11.7% | 13.5% | 15.5% | 19% | 22.2% | 10.8% | 13.6% | 15.5% | 19% | 22.2% | 10.8% | 14.2% | 18% | 19.8% | 22.2% | 12.3% | 10.2% | 27.6% | 21.7% | 7.4% | 17.2%
KIAMAL | 220 | 4.2% | 7.6% | 10.2% | 55.4% | 5.3% | 5.3% | 7.9% | 9.8% | 55.8% | 5.6% | 4.4% | 7.2% | 8.9% | 55.6% | 4.9% | 4.5% | 7.3% | 8.9% | 55.6% | 5% | 5.7% | 12.9% | 10.8% | 52.9% | 8.4% | 5.1% | 14% | 11.1% | 54.3% | 8.7%
KOORANGIE | 220 | 12.5% | 15.4% | 19.6% | 24.1% | 11% | 13.6% | 15.3% | 19% | 25.3% | 11% | 12.7% | 14.6% | 17.8% | 24.8% | 10.1% | 12.7% | 14.6% | 17.8% | 24.8% | 10.1% | 13.3% | 17.1% | 18.5% | 24.8% | 11.6% | 9.5% | 25.6% | 20.1% | 9.9% | 15.9%
LAVERTON NORTH | 220 | 12.4% | 53% | 48.1% | 0.9% | 42.6% | 12.2% | 52.1% | 47.6% | 1.3% | 42.2% | 11.5% | 54% | 46.7% | 1.1% | 41.9% | 11.5% | 54% | 46.7% | 1.1% | 41.9% | 11.1% | 53% | 46% | 1.4% | 41.2% | 10.4% | 48.9% | 44.3% | 1.9% | 38.9%
LOY YANG | 500 | 7.9% | 95.7% | 20.9% | 0.5% | 24.5% | 7.8% | 95.7% | 20.5% | 0.7% | 24.2% | 7.9% | 95.7% | 20.9% | 0.6% | 26.5% | 7.9% | 95.7% | 20.9% | 0.6% | 26.5% | 7.5% | 95.7% | 20.3% | 0.9% | 25.7% | 7.4% | 95.7% | 18.9% | 1.2% | 23.6%
MALVERN | 220 | 13.3% | 61.1% | 30.6% | 0.7% | 57.8% | 13.1% | 60.2% | 30% | 1.1% | 57.4% | 11.8% | 65.7% | 28.1% | 0.9% | 54.2% | 11.8% | 65.7% | 28.1% | 0.9% | 54.2% | 11.3% | 64.5% | 27.3% | 1.2% | 53.4% | 10.9% | 62% | 25.9% | 1.6% | 51.6%
MCKAY | 220 | 74.4% | 33.1% | 20.9% | 1.1% | 27.6% | 74.3% | 30.9% | 19.6% | 2% | 25.9% | 74% | 30.2% | 17.8% | 1.6% | 24% | 74% | 30.2% | 17.7% | 1.6% | 24% | 73.9% | 30% | 17.4% | 1.8% | 23.8% | 75.2% | 32.8% | 18.2% | 1.9% | 22.2%
MOORABOOL | 500 | 12.7% | 57.7% | 53.4% | 1% | 36.7% | 12.6% | 56.9% | 53% | 1.5% | 36.2% | 11.9% | 58.4% | 52.3% | 1.3% | 36.2% | 11.9% | 58.4% | 52.3% | 1.3% | 36.1% | 11.4% | 56.7% | 51.2% | 1.7% | 34.9% | 10.9% | 51.6% | 48.7% | 2.3% | 31.5%
MOORABOOL | 220 | 12.4% | 50.8% | 99.8% | 1.3% | 34.2% | 12.3% | 50.1% | 99.8% | 1.9% | 33.8% | 11.7% | 51.3% | 99.8% | 1.7% | 33.6% | 11.7% | 51.3% | 99.8% | 1.7% | 33.6% | 11.5% | 52.3% | 99.8% | 1.9% | 34% | 10.9% | 47.6% | 99.8% | 2.3% | 30.8%
MORTLAKE | 500 | 11.4% | 51.2% | 47.3% | 1.1% | 32.6% | 11.3% | 50.5% | 46.9% | 1.6% | 32.2% | 10.7% | 51.7% | 46.2% | 1.4% | 32.1% | 10.7% | 51.7% | 46.2% | 1.4% | 32.1% | 10.2% | 50.3% | 45.4% | 1.8% | 31% | 9.8% | 46% | 43.2% | 2.3% | 28%
MT BEAUTY | 220 | 78.9% | 35% | 22.1% | 1.2% | 29.2% | 78.8% | 32.6% | 20.7% | 2.1% | 27.4% | 78.5% | 32% | 18.8% | 1.7% | 25.4% | 78.5% | 31.9% | 18.7% | 1.7% | 25.3% | 78.4% | 31.7% | 18.4% | 1.9% | 25.2% | 79.7% | 34.7% | 19.2% | 2% | 23.5%
MURRA WARRA | 220 | 4.1% | 10.1% | 15.8% | 17.9% | 6.9% | 4.6% | 10.1% | 15.5% | 18.4% | 7% | 4.1% | 9.8% | 14.8% | 18.2% | 6.6% | 4.1% | 9.8% | 14.8% | 18.2% | 6.6% | 6.8% | 25% | 20.4% | 14.3% | 15.6% | 6.4% | 20.8% | 17.4% | 16.4% | 12.9%
MURRAY | 330 | 27.8% | 19.3% | 12% | 0.9% | 15.1% | 25% | 16.7% | 10.6% | 2% | 13.1% | 21.6% | 14.5% | 8.6% | 1.6% | 10.8% | 21.6% | 14.4% | 8.6% | 1.7% | 10.8% | 21.5% | 14.4% | 8.4% | 1.8% | 10.8% | 21.8% | 19.3% | 11.7% | 2.1% | 13.3%
NEWPORT | 220 | 12% | 47.8% | 32% | 0.7% | 52.5% | 11.7% | 47% | 31.5% | 1.1% | 52.2% | 11% | 49.3% | 30.4% | 0.9% | 51.7% | 11% | 49.3% | 30.4% | 0.9% | 51.7% | 10.5% | 48.2% | 29.7% | 1.1% | 51.1% | 9.6% | 45.2% | 28.5% | 1.5% | 50.6%
PINE LODGE | 220 | 68.3% | 29.5% | 22.9% | 2.1% | 23.1% | 68.5% | 27.5% | 21.6% | 3.3% | 21.6% | 68.2% | 26.6% | 19.8% | 2.8% | 19.9% | 68.2% | 26.6% | 19.8% | 2.8% | 19.9% | 68.5% | 27.2% | 19.7% | 3% | 20.3% | 66.8% | 29.9% | 20.6% | 2.2% | 20.4%
PLUMPTON | 500 | 11.3% | 53.2% | 36.1% | 0.7% | 33.2% | 11% | 52.4% | 35.6% | 1.1% | 32.7% | 10.5% | 53.8% | 34.9% | 1% | 32.7% | 10.5% | 53.8% | 34.9% | 1% | 32.7% | 9.9% | 51.4% | 33.8% | 1.3% | 31.1% | 9.6% | 46.7% | 31.1% | 1.9% | 27.9%
RED CLIFFS | 220 | 4.7% | 7.1% | 8.5% | 99.5% | 5% | 6.2% | 7.6% | 8.1% | 99.6% | 5.5% | 5.2% | 6.7% | 7% | 99.6% | 4.6% | 5.2% | 6.7% | 7% | 99.6% | 4.6% | 5.8% | 9.1% | 7.7% | 99.6% | 6.1% | 5% | 12.3% | 9.5% | 99.5% | 7.7%
RICHMOND | 220 | 14.5% | 61.4% | 31.4% | 0.7% | 52.9% | 14.2% | 60.4% | 30.8% | 1.2% | 52.3% | 13% | 64.9% | 29.1% | 1% | 50% | 13% | 64.9% | 29.1% | 1% | 50% | 12.5% | 63.6% | 28.3% | 1.2% | 49.1% | 12.2% | 61.1% | 26.8% | 1.7% | 47.2%
RINGWOOD | 220 | 13.9% | 59.7% | 31.5% | 0.7% | 72.8% | 13.6% | 58.7% | 30.9% | 1.2% | 72.5% | 12.5% | 63.4% | 29.1% | 0.9% | 70.3% | 12.5% | 63.4% | 29.1% | 0.9% | 70.3% | 11.9% | 62.1% | 28.3% | 1.2% | 69.7% | 11.3% | 59.5% | 27% | 1.7% | 68.4%
ROWVILLE | 500 | 12.2% | 73.7% | 31.6% | 0.7% | 38.8% | 11.9% | 73% | 31% | 1.1% | 38.3% | 11.3% | 75.3% | 30.3% | 0.9% | 38.4% | 11.3% | 75.3% | 30.3% | 0.9% | 38.3% | 10.8% | 73.8% | 29.4% | 1.2% | 37.1% | 10.7% | 71% | 27.4% | 1.7% | 34.1%
ROWVILLE BUS 1-2 | 220 | 13.7% | 65% | 31.2% | 0.7% | 48.6% | 13.4% | 64.1% | 30.6% | 1.1% | 48.1% | 12.2% | 69.5% | 28.8% | 0.9% | 45.3% | 12.2% | 69.5% | 28.8% | 0.9% | 45.3% | 11.7% | 68.2% | 28% | 1.2% | 44.3% | 12.5% | 66% | 26% | 1.6% | 39.7%
ROWVILLE BUS 3-4 | 220 | 13.7% | 62.8% | 31.5% | 0.7% | 59.4% | 13.4% | 61.8% | 30.9% | 1.2% | 59% | 12.2% | 67.6% | 28.9% | 0.9% | 55.8% | 12.2% | 67.6% | 28.9% | 0.9% | 55.8% | 11.6% | 66.3% | 28.1% | 1.2% | 54.9% | 11.2% | 63.8% | 26.6% | 1.6% | 53%
SHEPPARTON | 220 | 67.3% | 29.8% | 23.5% | 2.3% | 23.2% | 67.5% | 27.8% | 22.2% | 3.4% | 21.8% | 67.1% | 26.9% | 20.4% | 2.9% | 20.1% | 67.2% | 26.9% | 20.4% | 3% | 20.1% | 67.5% | 27.6% | 20.3% | 3.2% | 20.5% | 65.6% | 30.3% | 21.2% | 2.3% | 20.6%
SOUTH MORANG | 500 | 13.6% | 66% | 37.6% | 0.8% | 39.3% | 13.3% | 65% | 37% | 1.3% | 38.7% | 12.7% | 66.7% | 36.2% | 1.1% | 38.7% | 12.7% | 66.7% | 36.2% | 1.1% | 38.7% | 12% | 64.5% | 35.1% | 1.5% | 37.1% | 11.7% | 60.3% | 32.7% | 2% | 34%
SOUTH MORANG | 330 | 19.3% | 56.9% | 32.6% | 0.9% | 43.5% | 18.7% | 55.4% | 31.7% | 1.4% | 42.5% | 17.7% | 56.6% | 30.3% | 1.2% | 41.8% | 17.7% | 56.6% | 30.3% | 1.2% | 41.7% | 17.1% | 55% | 29.5% | 1.5% | 40.6% | 16.5% | 53.2% | 28.5% | 2% | 39.6%
SOUTH MORANG BUS 1 | 220 | 15.2% | 56.2% | 32.2% | 0.8% | 87% | 14.8% | 55.1% | 31.5% | 1.2% | 86.8% | 13.8% | 58% | 30% | 1% | 86.5% | 13.8% | 58% | 30% | 1% | 86.5% | 13.3% | 56.7% | 29.2% | 1.3% | 86.3% | 12.2% | 54.4% | 28.2% | 1.7% | 92.1%
SOUTH MORANG BUS 2 | 220 | 15.5% | 58.5% | 31.4% | 0.8% | 54.1% | 15.2% | 57.4% | 30.8% | 1.2% | 53.5% | 14.1% | 60.9% | 29.1% | 1% | 51.7% | 14.1% | 60.9% | 29.1% | 1% | 51.7% | 13.5% | 59.5% | 28.3% | 1.3% | 50.8% | 12.6% | 57.8% | 27.2% | 1.7% | 50.9%
SPRINGVALE | 220 | 13.6% | 62.2% | 31.1% | 0.7% | 58.8% | 13.3% | 61.2% | 30.6% | 1.1% | 58.4% | 12% | 66.9% | 28.6% | 0.9% | 55.2% | 12% | 66.9% | 28.6% | 0.9% | 55.2% | 11.5% | 65.7% | 27.8% | 1.2% | 54.3% | 11.1% | 63.2% | 26.4% | 1.6% | 52.5%
SYDENHAM | 500 | 13.3% | 62.8% | 42.5% | 0.9% | 39.2% | 13.1% | 61.9% | 42% | 1.4% | 38.6% | 12.4% | 63.6% | 41.2% | 1.2% | 38.6% | 12.4% | 63.6% | 41.2% | 1.2% | 38.6% | 11.7% | 60.8% | 39.9% | 1.6% | 36.7% | 11.4% | 55.2% | 36.8% | 2.2% | 33%
TARRONE | 500 | 10.9% | 49% | 45.3% | 1.1% | 31.2% | 10.9% | 48.4% | 44.9% | 1.6% | 30.8% | 10.3% | 49.6% | 44.3% | 1.4% | 30.7% | 10.3% | 49.5% | 44.3% | 1.4% | 30.7% | 9.9% | 48.2% | 43.4% | 1.8% | 29.7% | 9.5% | 44.1% | 41.4% | 2.3% | 26.9%
TARRONE | 132 | 9.7% | 43.6% | 40.2% | 1% | 27.8% | 9.7% | 43% | 39.9% | 1.5% | 27.4% | 9.2% | 44.1% | 39.3% | 1.3% | 27.3% | 9.2% | 44% | 39.3% | 1.3% | 27.3% | 8.8% | 42.9% | 38.6% | 1.6% | 26.4% | 8.4% | 39.2% | 36.8% | 2.1% | 23.9%
TEMPLESTOWE | 220 | 14.5% | 60% | 31.3% | 0.7% | 56.5% | 14.2% | 59% | 30.6% | 1.2% | 56% | 13% | 63.5% | 28.9% | 1% | 53.6% | 13% | 63.5% | 28.9% | 1% | 53.6% | 12.5% | 62.2% | 28.1% | 1.2% | 52.8% | 11.8% | 59.6% | 26.8% | 1.7% | 51.6%
TERANG | 220 | 10.2% | 37% | 69.3% | 1.6% | 25.1% | 10.1% | 36.5% | 69.2% | 2% | 24.7% | 9.6% | 37.2% | 69% | 1.8% | 24.5% | 9.6% | 37.2% | 69% | 1.8% | 24.5% | 9.9% | 40.4% | 70.1% | 1.8% | 26.2% | 9.2% | 36.6% | 69.1% | 2% | 23.6%
THOMASTOWN BUS 1 | 220 | 14.7% | 56.8% | 32.5% | 0.8% | 99.8% | 14.3% | 55.8% | 31.9% | 1.2% | 99.8% | 13.3% | 59.1% | 30.4% | 1% | 99.8% | 13.3% | 59% | 30.4% | 1% | 99.8% | 12.8% | 57.7% | 29.6% | 1.3% | 99.8% | 11.8% | 54.9% | 28.4% | 1.7% | 99.8%
THOMASTOWN BUS 2 | 220 | 15.6% | 57.8% | 32% | 0.8% | 58.6% | 15.3% | 56.8% | 31.4% | 1.2% | 58.1% | 14.2% | 60.3% | 29.8% | 1% | 56.4% | 14.2% | 60.3% | 29.8% | 1% | 56.4% | 13.7% | 59.1% | 29% | 1.3% | 55.7% | 11.6% | 55.7% | 28.1% | 1.7% | 57.7%
THOMASTOWN BUS 3 | 220 | 15.1% | 59.7% | 31.6% | 0.8% | 56.1% | 14.8% | 58.6% | 31% | 1.2% | 55.5% | 13.7% | 62.6% | 29.3% | 1% | 53.5% | 13.7% | 62.6% | 29.3% | 1% | 53.5% | 13.1% | 61.3% | 28.5% | 1.3% | 52.6% | 12.4% | 58.6% | 27.3% | 1.7% | 51.8%
TRAGOWEL | 500 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 10.2% | 30.5% | 22.9% | 4.6% | 18.8%
TRAGOWEL | 220 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 10.7% | 29.1% | 22.9% | 6.1% | 18.1%
TYABB | 220 | 12.5% | 64.8% | 29.5% | 0.7% | 43.5% | 12.3% | 64% | 29% | 1.1% | 43% | 11.3% | 68.4% | 27.5% | 0.9% | 41.2% | 11.3% | 68.3% | 27.5% | 0.9% | 41.2% | 10.8% | 67.2% | 26.7% | 1.2% | 40.2% | 11.4% | 65% | 24.9% | 1.6% | 36.2%
WAUBRA | 220 | 7.8% | 25.3% | 45.2% | 2.8% | 17.2% | 7.9% | 24.9% | 45.1% | 3.3% | 17% | 7.5% | 25.3% | 44.7% | 3.1% | 16.7% | 7.5% | 25.3% | 44.7% | 3.1% | 16.7% | 9.3% | 37.7% | 50% | 2.1% | 24.1% | 8.8% | 32% | 46.1% | 2.6% | 20.3%
WEMEN | 220 | 6.4% | 8.9% | 10.9% | 65.7% | 6.3% | 7.8% | 9.2% | 10.4% | 66.4% | 6.7% | 6.8% | 8.4% | 9.3% | 66.2% | 5.8% | 6.8% | 8.4% | 9.3% | 66.2% | 5.8% | 7.4% | 10.8% | 10% | 66.1% | 7.3% | 5.7% | 14.5% | 11.2% | 56.9% | 9.1%
WEST KIEWA | 220 | 78.1% | 34.7% | 21.8% | 1.2% | 28.9% | 78% | 32.3% | 20.5% | 2.1% | 27.1% | 77.7% | 31.6% | 18.6% | 1.7% | 25.1% | 77.7% | 31.6% | 18.6% | 1.7% | 25.1% | 77.5% | 31.4% | 18.2% | 1.9% | 24.9% | 78.9% | 34.3% | 19% | 2% | 23.3%
WEST MELBOURNE | 220 | 13% | 51.6% | 33.1% | 0.7% | 59.1% | 12.8% | 50.7% | 32.6% | 1.1% | 58.7% | 11.9% | 53.3% | 31.3% | 0.9% | 58.1% | 11.9% | 53.3% | 31.3% | 0.9% | 58.1% | 11.5% | 52.1% | 30.5% | 1.2% | 57.5% | 10.4% | 49% | 29.4% | 1.6% | 57.3%
WODONGA | 330 | 41.1% | 28.2% | 17.5% | 1.2% | 22.1% | 37.1% | 24.5% | 15.5% | 2.8% | 19.2% | 33.9% | 22.3% | 13.1% | 1.9% | 16.8% | 33.9% | 22.3% | 13.1% | 1.9% | 16.7% | 33.7% | 22.1% | 12.9% | 2.2% | 16.6% | 34.2% | 26.9% | 15.9% | 2.3% | 18.8%
YALLOURN | 220 | 12.9% | 60.2% | 29.6% | 0.7% | 51.2% | 12.6% | 59.3% | 29% | 1.1% | 50.8% | 10.1% | 78.1% | 25.1% | 0.8% | 39.4% | 10.1% | 78.1% | 25.1% | 0.8% | 39.4% | 9.7% | 77.3% | 24.4% | 1% | 38.5% | 9.7% | 75.8% | 22.9% | 1.4% | 35.9%