## Overview of the model
AVP System Strength RIT-T assessment
| Creation Date | 2025-04-03
| Client | AVP
| Description | System strength RIT-T model
Creators
Cell legend applied throughout the model
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## R1.1 - headline results
R1.1 - headline results
Interface for scenario settings and key results
Scenario settings
Sensitivities
|  | Core | High | Low
| Syncon expenditure | 1 | 1.3 | 0.7
| BESS expenditure | 1 | 1.25 | 0.75
| VER | 1 | 1.25 | 0.75
| Discount rate | 7% | 10.5% | 3.63%
Weighted NPV results
| Net present value ($, PV) |  |  |  |  | Weighted NPV results
| Portfolio |  | Value | Rank
| Base case | Base case | 0 | 6
| Option portfolio 1 | Option portfolio 1 | 3681557189.2897 | 5
| Option portfolio 2 | Option portfolio 2 | 3791517990.4164 | 4
| Option portfolio 3 | Option portfolio 3 | 3854765711.2248 | 2
| Option portfolio 4 | Option portfolio 4 | 3824593157.84 | 3
| Option portfolio OSW self-remediation | Option portfolio OSW self-remediation | 4037791459.6144 | 1
Benefit composition
Benefits
| Portfolio options |  | Capital expenditure | Operating expenditure | Avoided emissions | Avoided costs for non RIT-T proponents | Avoided fuel costs | Avoided unserved energy | Total
| Base case |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | -453189456.9255 | -41327365.2406 | 1199057418.8077 | 121451993.0127 | 1927071551.2682 | 928493048.3672 | 3681557189.2897
| Option portfolio 2 |  | -335467311.0355 | -30787995.283 | 1177824558.4736 | 122421817.7319 | 1929033872.1622 | 928493048.3672 | 3791517990.4164
| Option portfolio 3 |  | -311180694.5878 | -28944223.9004 | 1220515200.2085 | 123059389.3099 | 1922822991.8274 | 928493048.3672 | 3854765711.2248
| Option portfolio 4 |  | -342949420.972 | -33091568.8197 | 1230870778.1848 | 125493951.4436 | 1915776369.6361 | 928493048.3672 | 3824593157.84
| Option portfolio OSW self-remediation |  | -286100496.3803 | -27164837.0935 | 1302641864.8163 | 117622040.8258 | 2002299839.0789 | 928493048.3672 | 4037791459.6144
Differences in benefits
| Portfolio option | Relative to porfolio option | Capital expenditure | Operating expenditure | Avoided emissions | Avoided costs for non RIT-T proponents | Avoided fuel costs | Avoided unserved energy | Total
Option portfolio 1
| Option portfolio 2 | Option portfolio 1 | 117722145.89 | 10539369.9576 | -21232860.3341 | 969824.7192 | 1962320.894 | 0 | 109960801.1267
| Option portfolio 3 | Option portfolio 2 | 24286616.4477 | 1843771.3827 | 42690641.7349 | 637571.578 | -6210880.3349 | 0 | 63247720.8084
| Option portfolio 4 | Option portfolio 3 | -31768726.3843 | -4147344.9193 | 10355577.9763 | 2434562.1337 | -7046622.1913 | 0 | -30172553.3848
| Option portfolio OSW self-remediation | Option portfolio 3 | 25080198.2075 | 1779386.8069 | 82126664.6078 | -5437348.4841 | 79476847.2516 | 0 | 183025748.3896
| Option 1 |  |  |  | Option 2 |  |  |  | Option 3 | Option 4 | OSW sensitivity
[5 empty] | Option 2 relative to Option 1 |  |  |  | Option 3 relative to Option 2 | Option 4 relative to Option 3 | OSW sensitivity relative to Option 3

## R1.2 - capped EUE results
R1.2 - capped EUE results
Interface for scenario settings and key results
Scenario settings
Sensitivities
|  | Core | High | Low
| Syncon expenditure | 1 | 1.3 | 0.7
| BESS expenditure | 1 | 1.25 | 0.75
| VER | 1 | 1.25 | 0.75
| Discount rate | 7% | 10.5% | 3.63%
Weighted NPV results
| Net present value ($, PV) |  |  |  |  | Weighted NPV results
| Portfolio |  | Value | Rank
| Base case | Base case | 0 | 6
| Option portfolio 1 | Option portfolio 1 | 2753064140.9225 | 5
| Option portfolio 2 | Option portfolio 2 | 2863024942.0492 | 4
| Option portfolio 3 | Option portfolio 3 | 2926272662.8576 | 2
| Option portfolio 4 | Option portfolio 4 | 2896100109.4728 | 3
| Option portfolio OSW self-remediation | Option portfolio OSW self-remediation | 3109298411.2472 | 1
Benefit charts
Benefits
| Portfolio options |  | Capital expenditure | Operating expenditure | Avoided emissions | Avoided costs for non RIT-T proponents | Avoided fuel costs | Avoided unserved energy | Total
| Base case |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | -453189456.9255 | -41327365.2406 | 1199057418.8077 | 121451993.0127 | 1927071551.2682 | 0 | 2753064140.9225
| Option portfolio 2 |  | -335467311.0355 | -30787995.283 | 1177824558.4736 | 122421817.7319 | 1929033872.1622 | 0 | 2863024942.0492
| Option portfolio 3 |  | -311180694.5878 | -28944223.9004 | 1220515200.2085 | 123059389.3099 | 1922822991.8274 | 0 | 2926272662.8576
| Option portfolio 4 |  | -342949420.972 | -33091568.8197 | 1230870778.1848 | 125493951.4436 | 1915776369.6361 | 0 | 2896100109.4728
| Option portfolio OSW self-remediation |  | -286100496.3803 | -27164837.0935 | 1302641864.8163 | 117622040.8258 | 2002299839.0789 | 0 | 3109298411.2472
Differences in benefits
| Portfolio option | Relative to porfolio option | Capital expenditure | Operating expenditure | Avoided emissions | Avoided costs for non RIT-T proponents | Avoided fuel costs | Avoided unserved energy | Total
Option portfolio 1
| Option portfolio 2 | Option portfolio 1 | 117722145.89 | 10539369.9576 | -21232860.3341 | 969824.7192 | 1962320.894 | 0 | 109960801.1267
| Option portfolio 3 | Option portfolio 2 | 24286616.4477 | 1843771.3827 | 42690641.7349 | 637571.578 | -6210880.3349 | 0 | 63247720.8084
| Option portfolio 4 | Option portfolio 3 | -31768726.3843 | -4147344.9193 | 10355577.9763 | 2434562.1337 | -7046622.1913 | 0 | -30172553.3848
| Option portfolio OSW self-remediation | Option portfolio 3 | 25080198.2075 | 1779386.8069 | 82126664.6078 | -5437348.4841 | 79476847.2516 | 0 | 183025748.3896
| Option 1 |  |  |  | Option 2 |  |  |  | Option 3 | Option 4 | OSW sensitivity
[5 empty] | Option 2 relative to Option 1 |  |  |  | Option 3 relative to Option 2 | Option 4 relative to Option 3 | OSW sensitivity relative to Option 3

## R1.3 sensitivities - capped EUE
R1.3 sensitivities
Interface for CBA sensitivities
Sensitivities
+- syncon capex
| Option | 130% | 70%
| Base case | 0 | 0
| Option portfolio 1 | 2606812316.415 | 2899315965.4301
| Option portfolio 2 | 2756286689.1915 | 2969763194.9069
| Option portfolio 3 | 2827373526.3491 | 3025171799.3662
| Option portfolio 4 | 2786426151.5732 | 3005774067.3725
| Option portfolio OSW self-remediation | 3018074182.7342 | 3200522639.7603
|  | High syncon capex |  |  |  | Low syncon capex
+- 25% BESS capex
| Option | 125% | 75%
| Base case | 0 | 0
| Option portfolio 1 | 2751311455.8039 | 2754816826.0411
| Option portfolio 2 | 2860409659.5177 | 2865640224.5808
| Option portfolio 3 | 2923657380.3261 | 2928887945.3892
| Option portfolio 4 | 2893484826.9413 | 2898715392.0044
| Option portfolio OSW self-remediation | 3107002268.3063 | 3111594554.1881
|  | High BESS capex |  |  |  | Low BESS capex
+- 25% VER
| Option | 125% | 75%
| Base case | 0 | 0
| Option portfolio 1 | 3052828495.6244 | 2453299786.2206
| Option portfolio 2 | 3157481081.6676 | 2568568802.4308
| Option portfolio 3 | 3231401462.9098 | 2621143862.8055
| Option portfolio 4 | 3203817804.0191 | 2588382414.9266
| Option portfolio OSW self-remediation | 3434958877.4513 | 2783637945.0432
|  | High VER |  |  |  | Low VER
Low and high discount rate
| Option | 3.63% | 10.5%
| Base case | 0 | 0
| Option portfolio 1 | 3881361256.5794 | 1944810114.1318
| Option portfolio 2 | 3970962178.8806 | 2059155357.9659
| Option portfolio 3 | 4042341199.7778 | 2113427377.0835
| Option portfolio 4 | 4019697361.1402 | 2077278346.3981
| Option portfolio OSW self-remediation | 4285009455.3184 | 2251304927.7793
|  | 3.63% discount rate |  |  |  | 10.50% discount rate
Threshold values
| Boundary values | VER | Syncon capex | BESS capex | Discount rate
| PO3 not first ranked | 291.4% | 889.5% | 5020% | N/A

## I1 General Inputs
I1 General Inputs
Inputs and parameters for System Strength RIT-T assessment
General parameter and Portfolio inputs
General parameters
| Parameter |  | Unit | Value | Note
| First year of analysis |  | Year | 2026 | Earliest initiation of project portfolios
| Base year for dollar inputs |  | Year | 2024
| Analysis period |  | Years | 11
Option descriptions
| Option name |  | Option applicable 1/0 | Short description
| Base case |  | 1 | Existing synchronous generation only
| Option portfolio 1 |  | 1 | Existing generation plus committed/anticipated GFM BESS and new synchronous condensers
| Option portfolio 2 |  | 1 | The same technology types as option portfolio 1 plus upgrading additional GFL BESS to be GFM
| Option portfolio 3 |  | 1 | The same technology types as option portfolio 2 plus a GFM BESS from the IBR forecasts
| Option portfolio 4 |  | 1 | The same technology types as option portfolio 3, except with accelerated procurement of synchronous condensers
| Option portfolio OSW self-remediation |  | 1 | Gippsland and Portland offshore wind self-remediating sensitivity
Sensitivity inputs
Cost and benefit categories
Cost categories
Capital cost
Operating cost
| Benefit categories |  |  | Benefit input category
| Avoided fuel consumption from generation dispatch |  |  | Changes in fuel consumption
| Avoided voluntary load curtailment |  |  | Changes in voluntary load curtailment
| Avoided involuntary load shedding |  |  | Changes in involuntary load shedding
| Avoided costs for non RIT-T proponent parties |  |  | Changes in costs for non-RIT-T proponent parties
| Differences in the timing of expenditure |  |  | Differences in the timing of expenditure
| Changes in network losses |  |  | Network losses
| Avoided emissions |  |  | Greenhouse gas emissions
RIT market benefits
| NER | RIT-T market benefits
| 5.15A.2(c)(4)(i) | changes in fuel consumption arising through different patterns of generation dispatch
| 5.15A.2(c)(4)(ii) | changes in voluntary load curtailment
| 5.15A.2(c)(4)(iii) | changes in involuntary load shedding
| 5.15A.2(c)(4)(iv) | changes in costs for parties, other than the RIT-T proponent
| 5.15A.2(c)(4)(v) | differences in the timing of expenditure
| 5.15A.2(c)(4)(vi) | changes in network losses
| 5.15A.2(c)(4)(vii) | changes in ancillary services costs
| 5.15A.2(c)(4)(viii) | changes in Austraia's greenhouse gas emissions
| 5.15A.2(c)(4)(ix) | competition benefits
| 5.15A.2(c)(4)(x) | any additional option value
| 5.15A.2(c)(4)(xi) | other classes of market benefits

## I2.1 Capex
I2.1 Capex
Capex inputs for System Strength RIT-T assessment
| Capital cost inputs ($2023/24) | [5 empty] | All years refer to financial years
| Capital cost ($2023/24) | [5 empty] | Build period
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Base case | Existing generators | Existing Synchronous Generator | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Option portfolio 1 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7500000 | 250000 | 10 | 7500000
| Option portfolio 1 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2031 | 40 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | -164560000 | 4840000 | 6 | 164560000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2032 | 40 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | -169400000 | 4840000 | 5 | 169400000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2036 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | -188760000 | 4840000 | 1 | 188760000
| Option portfolio 1 | Synchronous Condenser Bulgana | Network Synchronous Condensers | 193600000 | 2033 | 40 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | -174240000 | 4840000 | 4 | 174240000
| Option portfolio 1 | Synchronous Condenser Kerang | Network Synchronous Condensers | 193600000 | 2035 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | -183920000 | 4840000 | 2 | 183920000
| Option portfolio 1 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 1 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 1 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1200000 | 100000 | 8 | 1200000
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Option portfolio 2 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7500000 | 250000 | 10 | 7500000
| Option portfolio 2 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | -164560000 | 4840000 | 6 | 164560000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2036 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | -188760000 | 4840000 | 1 | 188760000
| Option portfolio 2 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 2 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 2 | GFM BESS SSN Red Cliffs | Non-network BESS | 0 | 2035 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1200000 | 100000 | 8 | 1200000
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1166666.6667 | 166666.6667 | 5 | 1166666.6667
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1230769.2308 | 153846.1538 | 5 | 1230769.2308
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Option portfolio 3 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7500000 | 250000 | 10 | 7500000
| Option portfolio 3 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | -164560000 | 4840000 | 6 | 164560000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 3 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2035 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | -183920000 | 4840000 | 2 | 183920000
| Option portfolio 3 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 3 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1200000 | 100000 | 8 | 1200000
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1166666.6667 | 166666.6667 | 5 | 1166666.6667
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1230769.2308 | 153846.1538 | 5 | 1230769.2308
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Option portfolio 3 | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2032 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Option portfolio OSW self-remediation | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7500000 | 250000 | 10 | 7500000
| Option portfolio OSW self-remediation | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | -164560000 | 4840000 | 6 | 164560000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Red Cliffs | Non-network BESS | 0 | 2035 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1200000 | 100000 | 8 | 1200000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | -1500000 | 166666.6667 | 3 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | -1400000 | 200000 | 3 | 1400000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | -1454545.4545 | 181818.1818 | 3 | 1454545.4545
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | -1500000 | 166666.6667 | 3 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | -1500000 | 166666.6667 | 3 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning date | Economic life | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | Annual depreciation | Years in analysis | Terminal value
| Option portfolio 4 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7500000 | 250000 | 10 | 7500000
| Option portfolio 4 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2028 | 40 | 96800000 | 96800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -150040000 | 4840000 | 9 | 150040000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -154880000 | 4840000 | 8 | 154880000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | 0 | -179080000 | 4840000 | 3 | 179080000
| Option portfolio 4 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2035 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 64533333.3333 | 64533333.3333 | 64533333.3333 | 0 | -183920000 | 4840000 | 2 | 183920000
| Option portfolio 4 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 4 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1200000 | 100000 | 8 | 1200000
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1166666.6667 | 166666.6667 | 5 | 1166666.6667
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1230769.2308 | 153846.1538 | 5 | 1230769.2308
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 2000000 | 0 | 0 | 0 | 0 | -1285714.2857 | 142857.1429 | 5 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
| Option portfolio 4 | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2032 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0

## I2.2 Opex
I2.2 Opex
Opex inputs and parameters for System Strength RIT-T assessment
Operating cost inputs ($2023/24)
|  | Assumped opex | Unit | Value
|  | Existing Synchronous Generator | % | 1% | Per cent of capex
|  | Existing Synchronous Condenser | % | 0% | Per cent of capex
|  | Network Synchronous Condensers | % | 1% | Per cent of capex
|  | Non-network BESS | % | 0% | Per cent of capex
Opex
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case | Existing generators | Existing Synchronous Generator | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 1 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 100000 | 0 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Option portfolio 1 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2031 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2032 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2036 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000
| Option portfolio 1 | Synchronous Condenser Bulgana | Network Synchronous Condensers | 193600000 | 2033 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 1 | Synchronous Condenser Kerang | Network Synchronous Condensers | 193600000 | 2035 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000
| Option portfolio 1 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 2 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 100000 | 0 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Option portfolio 2 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 2 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2036 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000
| Option portfolio 2 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFM BESS SSN Red Cliffs | Non-network BESS | 0 | 2035 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 3 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 100000 | 0 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Option portfolio 3 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 3 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 3 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2035 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000
| Option portfolio 3 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2032 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio OSW self-remediation | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 100000 | 0 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Option portfolio OSW self-remediation | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2031 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Red Cliffs | Non-network BESS | 0 | 2035 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2034 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2034 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown | Non-network BESS | 0 | 2033 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option | Component | Asset class | Capex ($2023/24) | Commissioning | Economic life | Annual opex ($2023/24) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 4 | Existing generators | Existing Synchronous Generator | 10000000 | 2027 | 40 | 100000 | 0 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000 | 100000
| Option portfolio 4 | Existing Synchronous Condenser RCTS SSN | Existing Synchronous Condenser | 0 | 2026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2028 | 40 | 1936000 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2029 | 40 | 1936000 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000 | 1936000
| Option portfolio 4 | Synchronous Condenser Hazelwood | Network Synchronous Condensers | 193600000 | 2034 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000 | 1936000
| Option portfolio 4 | Synchronous Condenser Giffard (Gippsland) | Network Synchronous Condensers | 193600000 | 2035 | 40 | 1936000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1936000 | 1936000
| Option portfolio 4 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFM BESS SSN Moorabool | Non-network BESS | 0 | 2028 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2029 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood | Non-network BESS | 2000000 | 2032 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 2000000 | 2032 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool | Non-network BESS | 0 | 2033 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | ISP forecast GFM BESS SSN Hazelwood | Non-network BESS | 0 | 2032 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## I2.3 Market benefit inputs
I2.3 Market benefit inputs
Market benefit inputs for System Strength RIT-T assessment
'Market benefit' inputs ($2023/24)
For clarity, these inputs relate to forecast fuel costs across the NEM under each of the options (including the base case)
| Changes in fuel consumption | 5.15A.2(c)(4)(i)
| Portfolio name | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
| Base case | $, real | 2026: 2484208688.3509; 2027: 2224474563.8202; 2028: 2147825613.4827; 2029: 1789461577.2641; 2030: 1137331078.5196; 2031: 1422910665.3842; 2032: 1222309614.4819; 2033: 1698932914.551; 2034: 2395999222.5862; 2035: 1866407694.0108; 2036: 1878227553.2785
| Option portfolio 1 | $, real | 2026: 2484208688.3509; 2027: 2212104579.0626; 2028: 2097761491.7575; 2029: 1688089019.2776; 2030: 1094533368.2; 2031: 1194508801.1476; 2032: 616965037.4237; 2033: 791895480.746; 2034: 1734578670.9637; 2035: 1430943988.8103; 2036: 1322059506.7806
| Option portfolio 2 | $, real | 2026: 2484208688.3509; 2027: 2212104579.0626; 2028: 2097761491.7575; 2029: 1688089019.2776; 2030: 1094533368.2; 2031: 1194379487.3655; 2032: 612710194.3396; 2033: 790822374.8866; 2034: 1708913506.9694; 2035: 1453327453.0908; 2036: 1330146925.0732
| Option portfolio 3 | $, real | 2026: 2484208688.3509; 2027: 2212104579.0626; 2028: 2097761491.7575; 2029: 1688089019.2776; 2030: 1094533368.2; 2031: 1194379487.3655; 2032: 609554231.4424; 2033: 793729808.8511; 2034: 1725544641.1368; 2035: 1429947384.6369; 2036: 1350685797.208
| Option portfolio 4 | $, real | 2026: 2484208688.3509; 2027: 2212104579.0626; 2028: 2108057006.3645; 2029: 1688456432.9752; 2030: 1092927980.6705; 2031: 1194379487.3655; 2032: 609554231.4424; 2033: 793729808.8511; 2034: 1725544641.1368; 2035: 1429947384.6369; 2036: 1350685797.208
| Option portfolio OSW self-remediation | $, real | 2026: 2484208688.3509; 2027: 2212104579.0626; 2028: 2097761491.7575; 2029: 1688089019.2776; 2030: 1094533368.2; 2031: 1193818805.9013; 2032: 604615524.1991; 2033: 785472827.1076; 2034: 1683435889.6799; 2035: 1394295147.3329; 2036: 1275422093.9622
For clarity, these inputs relate to expected value of involuntary load shedding (or 'unserved energy') under each of the options (including the base case) - ie, the MWh forecast x VCR
| Changes in involuntary load shedding | 5.15A.2(c)(4)(iii)
| Portfolio name | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
| Base case | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 552388224.0435; 2034: 347513915.4647; 2035: 594246414.4986; 2036: 380732561.4652
| Option portfolio 1 | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0
| Option portfolio 2 | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0
| Option portfolio 3 | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0
| Option portfolio 4 | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0
| Option portfolio OSW self-remediation | $, real | 2026: 0; 2027: 0; 2028: 0; 2029: 0; 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0
For clarity, these inputs relate to the aggregate capex and opex (VOM & FOM) of generation and storage under each of the options (and the base case)
| Changes in costs for non-RIT-T proponent parties | 5.15A.2(c)(4)(iv)
| Portfolio name | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
| Base case | $, real | 2026: 3902716482.3676; 2027: 4024940394.25; 2028: 3797538556.4787; 2029: 3582215162.912; 2030: 3682235137.7007; 2031: 3940269693.1831; 2032: 4030879045.2673; 2033: 4150386464.7782; 2034: 3936249821.0592; 2035: 4110232587.5054; 2036: 4356107021.7845
| Option portfolio 1 | $, real | 2026: 3902716482.3676; 2027: 4034213849.2459; 2028: 3797557366.797; 2029: 3574698330.5746; 2030: 3675943602.5308; 2031: 3922830241.6459; 2032: 3997330186.7763; 2033: 4099412271.3238; 2034: 3889147734.7088; 2035: 4070761595.7143; 2036: 4314047125.7171
| Option portfolio 2 | $, real | 2026: 3902716482.3676; 2027: 4034213849.2459; 2028: 3797557366.797; 2029: 3574698330.5746; 2030: 3675943602.5308; 2031: 3922980207.2768; 2032: 3997351924.6664; 2033: 4099805958.0918; 2034: 3884784075.774; 2035: 4071984163.8592; 2036: 4314829588.1271
| Option portfolio 3 | $, real | 2026: 3902716482.3676; 2027: 4034213849.2459; 2028: 3797557366.797; 2029: 3574698330.5746; 2030: 3675943602.5308; 2031: 3922980207.2768; 2032: 3997225486.2407; 2033: 4098536174.4995; 2034: 3886403077.3112; 2035: 4070714832.7451; 2036: 4314619518.6991
| Option portfolio 4 | $, real | 2026: 3902716482.3676; 2027: 4034213849.2459; 2028: 3793183128.5164; 2029: 3575369001.9965; 2030: 3676580428.2293; 2031: 3922980207.2768; 2032: 3997225486.2407; 2033: 4098536174.4995; 2034: 3886403077.3112; 2035: 4070714832.7451; 2036: 4314619518.6991
| Option portfolio OSW self-remediation | $, real | 2026: 3902716482.3676; 2027: 4034213849.2459; 2028: 3797557366.797; 2029: 3574698330.5746; 2030: 3675943602.5308; 2031: 3922665944.5849; 2032: 4003831650.8951; 2033: 4103675911.1096; 2034: 3885656399.399; 2035: 4071057948.8115; 2036: 4312838243.6278
For clarity, these inputs relate to greenhouse gas emissions under each of the options (including the base case) - ie, the tonnes forecast x VER
| Greenhouse gas emissions | 5.15A.2(c)(4)(viii)
| Portfolio name | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045
| Base case | $, real | 2026: 8256000000; 2027: 7521367378.031; 2028: 7030678637.9746; 2029: 5977788793.7296; 2030: 4928933282.5287; 2031: 4624818384.3281; 2032: 3935736083.3425; 2033: 4553479353.4043; 2034: 2870461043.363; 2035: 1755149062.8566; 2036: 1914662560.011
| Option portfolio 1 | $, real | 2026: 8256000000; 2027: 7492800000; 2028: 6933100000; 2029: 5909000000; 2030: 4798500000; 2031: 4275000000; 2032: 3682800000; 2033: 4117500000; 2034: 2555000000; 2035: 1585700000; 2036: 1639300000
| Option portfolio 2 | $, real | 2026: 8256000000; 2027: 7492800000; 2028: 6933100000; 2029: 5909000000; 2030: 4798500000; 2031: 4278168666.3799; 2032: 3685609690.0858; 2033: 4156395072.7337; 2034: 2537202149.3639; 2035: 1596262387.0126; 2036: 1640420188.888
| Option portfolio 3 | $, real | 2026: 8256000000; 2027: 7492800000; 2028: 6933100000; 2029: 5909000000; 2030: 4798500000; 2031: 4278168666.3799; 2032: 3668415444.6251; 2033: 4089927355.1379; 2034: 2543257133.0976; 2035: 1583881044.27; 2036: 1654552331.0146
| Option portfolio 4 | $, real | 2026: 8256000000; 2027: 7492800000; 2028: 6927284969.8665; 2029: 5899882813.5199; 2030: 4799372087.3537; 2031: 4278168666.3799; 2032: 3668415444.6251; 2033: 4089927355.1379; 2034: 2543257133.0976; 2035: 1583881044.27; 2036: 1654552331.0146
| Option portfolio OSW self-remediation | $, real | 2026: 8256000000; 2027: 7492800000; 2028: 6933100000; 2029: 5909000000; 2030: 4798500000; 2031: 4260881854.7083; 2032: 3640494258.7085; 2033: 4075946986.2868; 2034: 2513457723.3958; 2035: 1560426957.6411; 2036: 1606771744.3369

## C1 Calculations
C1 Calculations
Calculating costs, benefits and NPV for each portfolio option
Incremental net present value calculation
| Net present value for each portfolio (uncapped EUE) |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Portfolio name |  | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 3681557189.2897 | -139066666.6667 | -97502758.874 | -48076050.6185 | 44639517.3868 | -18049471.9819 | 331618366.7687 | 625852185.5584 | 1678465871.3739 | 1228778930.1339 | 1158508841.0134 | 2794299064.0416
| Option portfolio 2 |  | $ | 3791517990.4164 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 447495715.2066 | 758278267.3332 | 1708655551.0649 | 1345010937.0325 | 1130148421.5755 | 2268811573.2056
| Option portfolio 3 |  | $ | 3854765711.2248 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 512029048.5399 | 778754914.117 | 1838018951.6218 | 1322641817.5941 | 1231712497.2194 | 2052366628.3721
| Option portfolio 4 |  | $ | 3824593157.84 | -235866666.6667 | -194302758.874 | 14415036.522 | 179849285.4141 | 173711002.4955 | 512029048.5399 | 778754914.117 | 1838018951.6218 | 1322641817.5941 | 1231712497.2194 | 2037846628.3721
| Option portfolio OSW self-remediation |  | $ | 4037791459.6144 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 540190804.3677 | 869541975.9557 | 1909649898.9396 | 1459829989.9984 | 1292411705.086 | 1996308160.0669
Present value of market benefits for each portfolio (uncapped EUE)
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 4176074011.4558 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 595659700.102 | 891829518.8917 | 1946379204.7072 | 1371497596.8006 | 1238630174.3468 | 1254323064.0416
| Option portfolio 2 |  | $ | 4157773296.7349 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 592470381.8732 | 893252933.9999 | 1908163551.0649 | 1419324270.3658 | 1204461754.9088 | 1244332994.451
| Option portfolio 3 |  | $ | 4194890629.7129 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 592470381.8732 | 913729580.7836 | 1972993618.2885 | 1395019150.9274 | 1241492497.2194 | 1209872049.6175
| Option portfolio 4 |  | $ | 4200634147.6317 | 0 | 31663907.7927 | 147517703.1887 | 185757285.4141 | 179619002.4955 | 592470381.8732 | 913729580.7836 | 1972993618.2885 | 1395019150.9274 | 1241492497.2194 | 1209872049.6175
| Option portfolio OSW self-remediation |  | $ | 4351056793.0882 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 610632137.701 | 939983309.289 | 1990091232.273 | 1467673989.9984 | 1300255705.086 | 1334697614.6123
Net present value for each portfolio (capped EUE) | bar: 2026 to 2036
| Portfolio name |  | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 2753064140.9225 | -139066666.6667 | -97502758.874 | -48076050.6185 | 44639517.3868 | -18049471.9819 | 331618366.7687 | 625852185.5584 | 1126077647.3304 | 881265014.6693 | 564262426.5148 | 2413566502.5764
| Option portfolio 2 |  | $ | 2863024942.0492 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 447495715.2066 | 758278267.3332 | 1156267327.0214 | 997497021.5678 | 535902007.0769 | 1888079011.7404
| Option portfolio 3 |  | $ | 2926272662.8576 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 512029048.5399 | 778754914.117 | 1285630727.5783 | 975127902.1294 | 637466082.7208 | 1671634066.9069
| Option portfolio 4 |  | $ | 2896100109.4728 | -235866666.6667 | -194302758.874 | 14415036.522 | 179849285.4141 | 173711002.4955 | 512029048.5399 | 778754914.117 | 1285630727.5783 | 975127902.1294 | 637466082.7208 | 1657114066.9069
| Option portfolio OSW self-remediation |  | $ | 3109298411.2472 | -139066666.6667 | -97502758.874 | -48076050.6185 | 109172850.7201 | 111017194.6848 | 540190804.3677 | 869541975.9557 | 1357261674.8961 | 1112316074.5337 | 698165290.5874 | 1615575598.6017
Present value of market benefits for each portfolio (capped EUE)
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 3247580963.0886 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 595659700.102 | 891829518.8917 | 1393990980.6637 | 1023983681.3359 | 644383759.8482 | 873590502.5764
| Option portfolio 2 |  | $ | 3229280248.3677 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 592470381.8732 | 893252933.9999 | 1355775327.0214 | 1071810354.9012 | 610215340.4102 | 863600432.9858
| Option portfolio 3 |  | $ | 3266397581.3458 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 592470381.8732 | 913729580.7836 | 1420605394.245 | 1047505235.4628 | 647246082.7208 | 829139488.1523
| Option portfolio 4 |  | $ | 3272141099.2646 | 0 | 31663907.7927 | 147517703.1887 | 185757285.4141 | 179619002.4955 | 592470381.8732 | 913729580.7836 | 1420605394.245 | 1047505235.4628 | 647246082.7208 | 829139488.1523
| Option portfolio OSW self-remediation |  | $ | 3422563744.721 | 0 | 31663907.7927 | 147623949.3815 | 177678184.0534 | 179522528.0181 | 610632137.701 | 939983309.289 | 1437703008.2294 | 1120160074.5337 | 706009290.5874 | 953965053.1471
Present value of costs for each portfolio
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | -494516822.1661 | -139066666.6667 | -129166666.6667 | -195700000 | -133038666.6667 | -197572000 | -264041333.3333 | -265977333.3333 | -267913333.3333 | -142718666.6667 | -80121333.3333 | 1539976000
| Option portfolio 2 |  | $ | -366255306.3185 | -139066666.6667 | -129166666.6667 | -195700000 | -68505333.3333 | -68505333.3333 | -144974666.6667 | -134974666.6667 | -199508000 | -74313333.3333 | -74313333.3333 | 1024478578.7546
| Option portfolio 3 |  | $ | -340124918.4881 | -139066666.6667 | -129166666.6667 | -195700000 | -68505333.3333 | -68505333.3333 | -80441333.3333 | -134974666.6667 | -134974666.6667 | -72377333.3333 | -9780000 | 842494578.7546
| Option portfolio 4 |  | $ | -376040989.7917 | -235866666.6667 | -225966666.6667 | -133102666.6667 | -5908000 | -5908000 | -80441333.3333 | -134974666.6667 | -134974666.6667 | -72377333.3333 | -9780000 | 827974578.7546
| Option portfolio OSW self-remediation |  | $ | -313265333.4738 | -139066666.6667 | -129166666.6667 | -195700000 | -68505333.3333 | -68505333.3333 | -70441333.3333 | -70441333.3333 | -80441333.3333 | -7844000 | -7844000 | 661610545.4545
Incremental cost calculation | bar: 2026 to 2036
Capital cost
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case | Existing generators |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 1 | Existing generators |  | -5404297.5884 | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500000
| Option portfolio 1 | Existing Synchronous Condenser RCTS SSN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 1 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 1 | Synchronous Condenser Hazelwood |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) |  | -65178222.6311 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 164560000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) |  | -53985150.4072 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 169400000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 1 | Synchronous Condenser Giffard (Gippsland) |  | -14754956.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 188760000
| Option portfolio 1 | Synchronous Condenser Bulgana |  | -43383745.2897 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 174240000
| Option portfolio 1 | Synchronous Condenser Kerang |  | -23803639.8449 | 0 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 183920000
| Option portfolio 1 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 | GFL to GFM BESS SSN Hazelwood |  | -992976.073 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200000
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 2 | Existing generators |  | -5404297.5884 | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500000
| Option portfolio 2 | Existing Synchronous Condenser RCTS SSN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 2 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 2 | Synchronous Condenser Hazelwood |  | -65178222.6311 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 164560000
| Option portfolio 2 | Synchronous Condenser Hazelwood |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 2 | Synchronous Condenser Giffard (Gippsland) |  | -14754956.2078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 188760000
| Option portfolio 2 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFM BESS SSN Red Cliffs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood |  | -992976.073 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200000
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood |  | -727485.5313 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1166666.6667
| Option portfolio 2 | GFL to GFM BESS SSN Hazelwood |  | -699023.2262 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1230769.2308
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 2 | GFL to GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 3 | Existing generators |  | -5404297.5884 | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500000
| Option portfolio 3 | Existing Synchronous Condenser RCTS SSN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 3 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 3 | Synchronous Condenser Hazelwood |  | -65178222.6311 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 164560000
| Option portfolio 3 | Synchronous Condenser Hazelwood |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 3 | Synchronous Condenser Giffard (Gippsland) |  | -23803639.8449 | 0 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 183920000
| Option portfolio 3 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood |  | -992976.073 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200000
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood |  | -727485.5313 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1166666.6667
| Option portfolio 3 | GFL to GFM BESS SSN Hazelwood |  | -699023.2262 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1230769.2308
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 3 | GFL to GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | ISP forecast GFM BESS SSN Hazelwood |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio OSW self-remediation | Existing generators |  | -5404297.5884 | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500000
| Option portfolio OSW self-remediation | Existing Synchronous Condenser RCTS SSN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood |  | -65178222.6311 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 164560000
| Option portfolio OSW self-remediation | Synchronous Condenser Hazelwood |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFM BESS SSN Red Cliffs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood |  | -992976.073 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood |  | -421849.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood |  | -466250.7422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 1400000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Hazelwood |  | -442031.9081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 1454545.4545
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool |  | -421849.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool |  | -421849.5463 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 1500000
| Option portfolio OSW self-remediation | GFL to GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Hazelwood |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation | ISP forecast GFM BESS SSN Thomastown |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio name | Component |  | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Option portfolio 4 | Existing generators |  | -5404297.5884 | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7500000
| Option portfolio 4 | Existing Synchronous Condenser RCTS SSN |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | Synchronous Condenser Hazelwood |  | -96946949.0154 | -96800000 | -96800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150040000
| Option portfolio 4 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 4 | Synchronous Condenser Hazelwood |  | -89507934.3568 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154880000
| Option portfolio 4 | Synchronous Condenser Hazelwood |  | -33335300.0848 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 0 | 179080000
| Option portfolio 4 | Synchronous Condenser Giffard (Gippsland) |  | -23803639.8449 | 0 | 0 | 0 | 0 | 0 | 0 | -64533333.3333 | -64533333.3333 | -64533333.3333 | 0 | 183920000
| Option portfolio 4 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood |  | -992976.073 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200000
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood |  | -727485.5313 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1166666.6667
| Option portfolio 4 | GFL to GFM BESS SSN Hazelwood |  | -699023.2262 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1230769.2308
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool |  | -674626.9647 | 0 | 0 | 0 | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 1285714.2857
| Option portfolio 4 | GFL to GFM BESS SSN Moorabool |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | ISP forecast GFM BESS SSN Hazelwood |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital cost
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | -453189456.9255 | -139066666.6667 | -129066666.6667 | -195600000 | -129066666.6667 | -193600000 | -258133333.3333 | -258133333.3333 | -258133333.3333 | -129066666.6667 | -64533333.3333 | 1557500000
| Option portfolio 2 |  | $ | -335467311.0355 | -139066666.6667 | -129066666.6667 | -195600000 | -64533333.3333 | -64533333.3333 | -139066666.6667 | -129066666.6667 | -193600000 | -64533333.3333 | -64533333.3333 | 1036194578.7546
| Option portfolio 3 |  | $ | -311180694.5878 | -139066666.6667 | -129066666.6667 | -195600000 | -64533333.3333 | -64533333.3333 | -74533333.3333 | -129066666.6667 | -129066666.6667 | -64533333.3333 | 0 | 852274578.7546
| Option portfolio 4 |  | $ | -342949420.972 | -235866666.6667 | -225866666.6667 | -131066666.6667 | 0 | 0 | -74533333.3333 | -129066666.6667 | -129066666.6667 | -64533333.3333 | 0 | 837754578.7546
| Option portfolio OSW self-remediation |  | $ | -286100496.3803 | -139066666.6667 | -129066666.6667 | -195600000 | -64533333.3333 | -64533333.3333 | -64533333.3333 | -64533333.3333 | -74533333.3333 | 0 | 0 | 669454545.4545
Capex stream (excl terminal value)
[5 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Option portfolio 1 | New Syncons |  |  | -129066666.6667 | -129066666.6667 | -193600000 | -129066666.6667 | -193600000 | -258133333.3333 | -258133333.3333 | -258133333.3333 | -129066666.6667 | -64533333.3333
|  | Upgrading GFL to GFM BESS |  |  | 0 | 0 | -2000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Existing generators |  |  | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 | New Syncons |  |  | -129066666.6667 | -129066666.6667 | -193600000 | -64533333.3333 | -64533333.3333 | -129066666.6667 | -129066666.6667 | -193600000 | -64533333.3333 | -64533333.3333
|  | Upgrading GFL to GFM BESS |  |  | 0 | 0 | -2000000 | 0 | 0 | -10000000 | 0 | 0 | 0 | 0
|  | Existing generators |  |  | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 | New Syncons |  |  | -129066666.6667 | -129066666.6667 | -193600000 | -64533333.3333 | -64533333.3333 | -64533333.3333 | -129066666.6667 | -129066666.6667 | -64533333.3333 | 0
|  | Upgrading GFL to GFM BESS |  |  | 0 | 0 | -2000000 | 0 | 0 | -10000000 | 0 | 0 | 0 | 0
|  | Existing generators |  |  | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 | New Syncons |  |  | -225866666.6667 | -225866666.6667 | -129066666.6667 | 0 | 0 | -64533333.3333 | -129066666.6667 | -129066666.6667 | -64533333.3333 | 0
|  | Upgrading GFL to GFM BESS |  |  | 0 | 0 | -2000000 | 0 | 0 | -10000000 | 0 | 0 | 0 | 0
|  | Existing generators |  |  | -10000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operating cost
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | -41327365.2406 | 0 | -100000 | -100000 | -3972000 | -3972000 | -5908000 | -7844000 | -9780000 | -13652000 | -15588000 | -17524000
| Option portfolio 2 |  | $ | -30787995.283 | 0 | -100000 | -100000 | -3972000 | -3972000 | -5908000 | -5908000 | -5908000 | -9780000 | -9780000 | -11716000
| Option portfolio 3 |  | $ | -28944223.9004 | 0 | -100000 | -100000 | -3972000 | -3972000 | -5908000 | -5908000 | -5908000 | -7844000 | -9780000 | -9780000
| Option portfolio 4 |  | $ | -33091568.8197 | 0 | -100000 | -2036000 | -5908000 | -5908000 | -5908000 | -5908000 | -5908000 | -7844000 | -9780000 | -9780000
| Option portfolio OSW self-remediation |  | $ | -27164837.0935 | 0 | -100000 | -100000 | -3972000 | -3972000 | -5908000 | -5908000 | -5908000 | -7844000 | -7844000 | -7844000
Incremental 'market benefits' calculation
Avoided fuel consumption from generation dispatch
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 1927071551.2682 | 0 | 12369984.7575 | 50064121.7252 | 101372557.9865 | 42797710.3196 | 228401864.2366 | 605344577.0582 | 907037433.805 | 661420551.6225 | 435463705.2005 | 556168046.498
| Option portfolio 2 |  | $ | 1929033872.1622 | 0 | 12369984.7575 | 50064121.7252 | 101372557.9865 | 42797710.3196 | 228531178.0188 | 609599420.1424 | 908110539.6643 | 687085715.6168 | 413080240.92 | 548080628.2054
| Option portfolio 3 |  | $ | 1922822991.8274 | 0 | 12369984.7575 | 50064121.7252 | 101372557.9865 | 42797710.3196 | 228531178.0188 | 612755383.0396 | 905203105.6999 | 670454581.4494 | 436460309.3738 | 527541756.0706
| Option portfolio 4 |  | $ | 1915776369.6361 | 0 | 12369984.7575 | 39768607.1182 | 101005144.2889 | 44403097.8491 | 228531178.0188 | 612755383.0396 | 905203105.6999 | 670454581.4494 | 436460309.3738 | 527541756.0706
| Option portfolio OSW self-remediation |  | $ | 2002299839.0789 | 0 | 12369984.7575 | 50064121.7252 | 101372557.9865 | 42797710.3196 | 229091859.483 | 617694090.2828 | 913460087.4434 | 712563332.9063 | 472112546.6779 | 602805459.3163
Avoided involuntary load shedding (uncapped EUE)
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 928493048.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552388224.0435 | 347513915.4647 | 594246414.4986 | 380732561.4652
| Option portfolio 2 |  | $ | 928493048.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552388224.0435 | 347513915.4647 | 594246414.4986 | 380732561.4652
| Option portfolio 3 |  | $ | 928493048.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552388224.0435 | 347513915.4647 | 594246414.4986 | 380732561.4652
| Option portfolio 4 |  | $ | 928493048.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552388224.0435 | 347513915.4647 | 594246414.4986 | 380732561.4652
| Option portfolio OSW self-remediation |  | $ | 928493048.3672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 552388224.0435 | 347513915.4647 | 594246414.4986 | 380732561.4652
Avoided involuntary load shedding (capped EUE)
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 2 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio OSW self-remediation |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided costs for non RIT-T proponent parties
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 121451993.0127 | 0 | -9273454.9959 | -18810.3183 | 7516832.3374 | 6291535.1699 | 17439451.5372 | 33548858.491 | 50974193.4544 | 47102086.3504 | 39470991.7911 | 42059896.0674
| Option portfolio 2 |  | $ | 122421817.7319 | 0 | -9273454.9959 | -18810.3183 | 7516832.3374 | 6291535.1699 | 17289485.9063 | 33527120.6009 | 50580506.6864 | 51465745.2852 | 38248423.6462 | 41277433.6574
| Option portfolio 3 |  | $ | 123059389.3099 | 0 | -9273454.9959 | -18810.3183 | 7516832.3374 | 6291535.1699 | 17289485.9063 | 33653559.0266 | 51850290.2787 | 49846743.748 | 39517754.7603 | 41487503.0853
| Option portfolio 4 |  | $ | 125493951.4436 | 0 | -9273454.9959 | 4355427.9624 | 6846160.9155 | 5654709.4714 | 17289485.9063 | 33653559.0266 | 51850290.2787 | 49846743.748 | 39517754.7603 | 41487503.0853
| Option portfolio OSW self-remediation |  | $ | 117622040.8258 | 0 | -9273454.9959 | -18810.3183 | 7516832.3374 | 6291535.1699 | 17603748.5982 | 27047394.3722 | 46710553.6686 | 50593421.6602 | 39174638.6939 | 43268778.1567
Avoided emissions
| Portfolio name |  | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Base case |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  | $ | 1199057418.8077 | 0 | 28567378.031 | 97578637.9746 | 68788793.7296 | 130433282.5287 | 349818384.3281 | 252936083.3425 | 435979353.4043 | 315461043.363 | 169449062.8566 | 275362560.011
| Option portfolio 2 |  | $ | 1177824558.4736 | 0 | 28567378.031 | 97578637.9746 | 68788793.7296 | 130433282.5287 | 346649717.9482 | 250126393.2566 | 397084280.6706 | 333258893.9992 | 158886675.844 | 274242371.1231
| Option portfolio 3 |  | $ | 1220515200.2085 | 0 | 28567378.031 | 97578637.9746 | 68788793.7296 | 130433282.5287 | 346649717.9482 | 267320638.7174 | 463551998.2664 | 327203910.2654 | 171268018.5866 | 260110228.9964
| Option portfolio 4 |  | $ | 1230870778.1848 | 0 | 28567378.031 | 103393668.1082 | 77905980.2097 | 129561195.175 | 346649717.9482 | 267320638.7174 | 463551998.2664 | 327203910.2654 | 171268018.5866 | 260110228.9964
| Option portfolio OSW self-remediation |  | $ | 1302641864.8163 | 0 | 28567378.031 | 97578637.9746 | 68788793.7296 | 130433282.5287 | 363936529.6199 | 295241824.634 | 477532367.1175 | 357003319.9672 | 194722105.2156 | 307890815.6741
Capital stream (excl terminal value) calculations
| Discount factor |  |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036
| Discount factor |  |  |  | 87.34% | 81.63% | 76.29% | 71.3% | 66.63% | 62.27% | 58.2% | 54.39% | 50.83% | 47.51%
Capex stream (PV, excluding terminal value)
| Portfolio name |  |  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Base case |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Option portfolio 1 |  |  |  | -121466212.4785 | -105356845.9774 | -149222303.4765 | -92022749.5654 | -129003854.5309 | -160752466.7051 | -150235950.1917 | -140407430.0857 | -65610948.6382 | -30659321.7935
| Option portfolio 2 |  |  |  | -121466212.4785 | -105356845.9774 | -149222303.4765 | -46011374.7827 | -43001284.8436 | -86603730.7714 | -75117975.0959 | -105305572.5643 | -32805474.3191 | -30659321.7935
| Option portfolio 3 |  |  |  | -121466212.4785 | -105356845.9774 | -149222303.4765 | -46011374.7827 | -43001284.8436 | -46415614.0951 | -75117975.0959 | -70203715.0429 | -32805474.3191 | 0
| Option portfolio 4 |  |  |  | -206015081.3754 | -184374480.4604 | -99990132.459 | 0 | 0 | -46415614.0951 | -75117975.0959 | -70203715.0429 | -32805474.3191 | 0
| Option portfolio OSW self-remediation |  |  |  | -121466212.4785 | -105356845.9774 | -149222303.4765 | -46011374.7827 | -43001284.8436 | -40188116.6763 | -37558987.5479 | -40541194.9473 | 0 | 0