## Introduction
In December 2018, AER made a final determination on a new Transmission Annual Planning Report (TAPR) Guideline, requiring TNSPs to publish specified information on emerging transmission line and terminal station limitations.
The "Summary of Transmission connection point (TCP) data" spreadsheet provides information on a selected set of transmission terminal stations associated with Declared Shared Network(DSN) transformer emerging limitations and connection asset limitations.
The DSN transformer priority limitations were selected based on AEMO’s VAPR and RIT-T reports, and the connection asset limitations were selected based on the 2024 Transmission Connection Planning report (TCPR), produced jointly by the Victorian Electricity Distribution Businesses.
As AEMO's RIT-T projects are still works in progress, the information provided is subject to change.
The general criteria for selecting the existing assets to be included in the data reporting are:
• For DSN assets, they are associated with both load and generation driven priority or monitored limitations for which AEMO has yet to finalise the preferred option to address.
• For connection assets , their augmentations are required in the near future according to the 2024 TCPR.
For connection assets, the information is purely based on that available in the 2024 TCPR. AEMO has noted that some Victorian DNSPs may use their own connection point demand forecast, which is different from AEMO’s connection point demand forecast
In addition to the information on priority limitations specified in the TAPR guideline, The "Summary of TCP data sheet" also includes information related to terminal stations with monitored limitations, and other terminal stations in Vic.
The information on monitored limitations includes:
• Constrained connection point ID
• Constraint primary driver
• Constraint investment type
• Constrained connection point location
• Voltage level
• Preferred investment— Description
• Preferred investment — Capital cost (if available)
• Preferred investment— Cost accuracy (if available)
• Maximum fault level
The information on other terminal stations not associated with any limitation includes terminal station location, voltage level and maximum fault level at the high voltage side.

## Summary of TCP data 2021 (hidden)
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melourne & Geelong | Emerging | Altona West terminal station | Customer load at risk (market benefit) | Augmentation | 37.839oS, 144.789oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast spreadsheet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits | $18M | Unavailable from TCPR | Unavailable from TCPR | 2026 | 9 MW | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 158 MW (summer) | Unavailable from TCPR | Unavailable from TCPR | 19kA (66kV) | $1.79M in 2029 | $34,740/MWh | 51.6 MWh in 2029 | 51.5256
| Emerging | Cranbourne terminal station | Customer load at risk (market benefit) | Augmentation | 38.085oS, 145.265oE | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 4th 150MVA transformer | $26M | Unavailable from TCPR | Unavailable from TCPR | 2023 | 7MW (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 359MVA | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $2.46M in 2026 | $34,778/MWh | 70.8MWh in 2026 | 51.581
| Emerging | Deer Park terminal station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast spreadseet" | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | 3rd 225MVA transformer, initially "spare", not terminated. | $4M | Unavailable from TCPR | [9 empty] | 11kA (66kV) | $0.45M in 2026 | $38,272/MWh | 11.8MWh in 2026
| Monitored | South Morang terminal station | Increased demand in Metropolitan Melbourne and/or increased import from NSW. | Augmentation | 37.644⁰ S 145.078⁰ E | [7 empty] | 330/220kV |  |  | Replace the existing transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $44M |  | not available | 2024 | Not applicable | [6 empty] | 25kA (330kV)
| Developing | Cranbourne terminal station | Increased demand around the Eastern Melbourne Metropolitan area. | Augmentation | 38.085oS, 145.265oE | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $72.5M |  | 50% | [8 empty] | 17kA (500kV)
| Developing | Rowville terminal station | Increased demand in Eastern Metropolitan Melbourne. | Augmentation | 37.928⁰ S 145.226⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity at Cranbourne terminal station. | $72.5M |  | 50% | [8 empty] | 21kA (500kV)
Murray River REZ | Emerging | Wemen terminal station | Posible increased generation embedded inte distribution network. | Augmentation | 34.791⁰ S 142.522⁰ E | [7 empty] | 220kV |  |  | Install additional transformation capacity at Wemen terminal station. | Unavailable from TCPR | [10 empty] | 5kA
South - West Victoria REZ | Developing | Moorabool terminal station | Large-scale new generation in western Victoria area | Augmentation | 38.037⁰ S 144.296⁰ E | [7 empty] | 500/220kV |  |  | Install additional transformation capacity | $102M |  | 50% | [8 empty] | 17kA (500kV)
Ovens Murray REZ | Developing | Dederang terminal station | High imports from NSW and Murray generation (with the DBUSS transformer control scheme being active). | Augmentation | 36.454⁰ S 146.992⁰ E | [7 empty] | 330/220kV |  |  | Install additional transformation capacity | Unavailable |  | 50% | [8 empty] | 18kA (330kV)
Eastern Corridor |  | Hazelwood terminal station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 27kA
|  | Hazelwood power station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 41kA
|  | Jeeralang terminal station |  |  | 38.275⁰ S 146.425⁰ E | [7 empty] | 220kV | [14 empty] | 33kA
|  | Loy Yang power staton |  |  | 38.254⁰ S 146.576⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Morwell terminal station |  |  | 38.259⁰ S 146.421⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
|  | Yallourn terminal station |  |  | 38.177⁰ S 146.344⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
Ovens Murray REZ |  | Wodonga terminal station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 10kA
|  | Mt Beauty terminal station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Eildon terminal station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Dartmouth terminal station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Mckay Creek terminal station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | West Kiewa terminal station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Bogong terminal station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | East Rowville terminal station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 220kV | [14 empty] | 32kA
|  | Tyabb terminal station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | Western Port terminal station |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 15kA
|  | Malvern terminal station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Springvale terminal station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Heatherton terminal station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Ringwood terminal station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Templestowe terminal station |  |  | 37.749⁰ S 145.171⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Thomastown terminal station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 220kV | [14 empty] | 29kA
|  | Richmond terminal station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 220kV | [14 empty] | 26kA
|  | Brunswick terminal station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Keilor terminal station |  |  | 37.738⁰ S 144.846⁰ E | [7 empty] | 500kV | [14 empty] | 30kA
|  | West Melbourne terminal station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Fishermans Bend terminal station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Brooklyn terminal station |  |  | 37.826⁰ S 144.86⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Newport terminal station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Laverton North terminal station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Geelong terminal station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 220kV | [14 empty] | 25kA
Central North REZ |  | Fosterville terminal station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Glenrowan terminal station |  |  | 36.494⁰ S 146.075⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Shepparton terminal station |  |  | 36.353⁰ S 145.365⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
Murray River REZ |  | Bendigo terminal station |  |  | 36.796⁰ S 144.252⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Kerang terminal station |  |  | 35.782⁰ S 143.945⁰ E | [7 empty] | 220kV | [14 empty] | 4kA
|  | Kiamal terminal station |  |  | 35.027⁰ S 142.299⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Red Cliffs terminal station |  |  | 34.275⁰ S 142.2⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
South West Victoria REZ |  | Heywood terminal station |  |  | 38.182⁰ S 141.638⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Berrybank substation |  |  | 37.900⁰ S 143.438⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Blue Gum substation |  |  | 38.067⁰ S 142.674⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Haunted Gully terminal station |  |  | 38.006⁰ S 143.317⁰ E | [7 empty] | 500kV | [14 empty] | 13kA
|  | Mortlake terminal station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Portland substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 28kA
|  | Tarrone terminal station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 8kA
|  | Terang terminal station |  |  | 38.256⁰ S 142.925⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
Western Victoria REZ |  | Ararat terminal station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Ballarat terminal station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Bulgana terminal station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | Crowlands terminal station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Elaine terminal station |  |  | 37.731⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Horsham terminal station |  |  | 36.731⁰ S 142.246⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Murra Warra terminal station |  |  | 36.455⁰ S 142.321⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Waubra terminal station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
South Morang project annual deferral value is present value of a one year deferment of project cost, using 6% pa discount rate.
Altona West, Cranbourne, and Deer Park Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
[13 empty] | 50pcl | 10pcl | $M
[9 empty] | $M pa | $M capex |  | VCR | MWh | MWh |  | MWh
[8 empty] | ATS W | 1.33 | 18 | 0.073889 | 34740 | 43.07 | 71.44 | 1.7919 | 51.581 | 1.7919
[8 empty] | CBTS | 1.9 | 26 | 0.073077 | 34778 | 21 | 187 | 2.4623 | 70.8 | 2.4623
[8 empty] | DPTS | 0.3 | 4.0826 | 0.073483 | 38272 | 5.32 | 26.78 | 0.45 | 11.758 | 0.45

## Summary of TCP data
Region | Limitation Type | Constrained connection point ID | Constraint primary driver | Constraint investment type | Constrained connection point location | Annual energy and peak demand of residential customers affected | Annual energy and peak demand of industrial customers affected | Annual energy and peak demand of commercial customers affected | Forecast 10% and 50% Probability of Exceedance (POE) peak demand on maximum demand day | Maximum demand on minimum demand day | Forecast daily demand profile on maximum demand day | Forecast daily demand profile on minimum demand day | Voltage level | Forecast maximum load at risk per year | Connection point load duration curve data | Preferred investment— Description | Preferred investment — Capital cost | Preferred investment — Annual network operating cost | Preferred investment— Cost accuracy | Preferred investment— Proposed timing | Demand reduction required to defer investment by 1 year | Annual deferral value | Load transfer capacity | Historic load trace | Historic connection point rating | Limitation asset | Unplanned outages | Maximum fault level | Annual economic cost of constraint | VCR | Annual expected unserved energy
Greater Melbourne & Geelong | Priority | Altona/Brooklyn Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.826⁰S, 144.860⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona_Brooklyn MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits at ATS or BLTS | $35M | $0.35M | Unavailable from TCPR | 2028 | 53 MVA (50th percentile) | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 339 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 21kA (66kV) | $3.2M in 2028 | $51,115/MWh | 63.5 MWh in 2028
| Priority | Altona West Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.839⁰S, 144.789⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Altona West MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install additional transformation capacity and reconfigure 66 kV exits at ATS | $35M | $0.35M | Unavailable from TCPR | 2028 | 91 MW (50th percentile) | Unavailable from TCPR | 24 MVA (in summer 2024) | Unavailable from TCPR | 170 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 19kA (66kV) | $16.6M in 2028 | $40,420/MWh | 409.4 MWh in 2028
| Priority | Cranbourne Terminal Station | Customer load at risk (market benefit) | Augmentation | 38.085⁰S, 145.265⁰E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Cranbourne MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install a fourth transformer | $63M (2025 AusNet & United Energy RIT-T, PACR) | $0.6M (2025 AusNet & United Energy RIT-T, PACR) | Unavailable from TCPR | 2026/27 | 13 MVA (50th percentile) | Unavailable from TCPR | 70 MVA via 22kV network and 260 MVA via 66kV network. | Unavailable from TCPR | 369MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 22kA (66kV) | $3.99M in 2026/27 | $39,600/MWh | 101 MWh in 2026/27
| Priority | Deer Park Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.778⁰ S 144.735⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Deer Park MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install a third transformer | $35M | $0.35M | Unavailable from TCPR | 2027 | 94 MVA (50th percentile) | Unavailable from TCPR | 27 MVA (in summer 2024) | Unavailable from TCPR | 280 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 12kA (66kV) | $4.2M in 2027 | $46,304/MWh | 90.3 MWh in 2027
| Priority | Keilor Terminal Station (B1,2,5) | Customer load at risk (market benefit) | Augmentation | 37.738⁰ S 144.846⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Keilor MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Upgrade transformation capacity at KTS (B1,2,5) group and install additional transformation capacity at KTS (B3,4) group | $91M | $0.9M | Unavailable from TCPR | 2028 | 87 MVA (50th percentile) | Unavailable from TCPR | 20 MVA (in summer 2025) | Unavailable from TCPR | 393 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 23kA (66kV) | $17M in 2028 | $47,760/MWh | 356.4 MWh in 2028
| Priority | South Morang Terminal Station | Customer load at risk (market benefit) | Augmentation | 37.644⁰ S 145.078⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "South Morang MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 66kV | Unavailable from TCPR | Unavailable from TCPR | Install a third 225 MVA 220/66kV transformer. | $43.6M | $0.436M | Unavailable from TCPR | 2026 | 19 MVA (50th percentile) | Unavailable from TCPR | 36 MVA | Unavailable from TCPR | 265 MVA (summer N-1 import) | Unavailable from TCPR | Unavailable from TCPR | 21kA (66kV) | $5.4M in 2026 | $41,449/MWh | 130 MWh in 2026
| Monitored | Cranbourne Terminal Station | Increased demand around the Eastern Melbourne Metropolitan area. Reduced supply in 220 kV metro network and increased supply from 500 kV network. | Augmentation | 38.085oS, 145.265oE | [7 empty] | 500/220kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR |  | Install a new 500/220 kV 1,000 MVA transformer at Cranbourne Terminal Station and cut in the existing Hazelwood – Rowville No.3 500 kV line at Cranbourne. | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR | [10 empty] | 19kA (500kV) 31kA (220kV) |  | $48,152/MWh | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR
| Priority | Keilor Terminal Station | Increased maximum demand in Metropolitan Melbourne. | Replacement | 37.738⁰ S 144.846⁰ E | [7 empty] | 500/220kV |  |  | Replace the existing A2, A3, A4 500/220 kV transformers with higher rated units in conjunction with AusNet Service’s asset replacement program. | $305M (includes additional works, AusNet Asset Renewal Plan 2025) |  |  | 2031 (AusNet Asset Renewal Plan 2025) | Not applicable |  |  | Refer transmission line segment data sheet |  |  |  | 23kA (500kV) 32kA (220kV)
| Priority | Rowville Terminal Station | Increased demand in Eastern Metropolitan Melbourne or Reduced 220kV infeed from Latrobe Valley and increased supply from Western Victoria | Augmentation | 37.929⁰ S 145.227⁰ E | [7 empty] | 500/220kV | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR |  | Install additional transformation capacity at Rowville Terminal Station, or change switching arrangement for Rowville A2 transformer and install additional transformer at Cranbourne Terminal Station. | $76.40M transformer cost (Eastern Victoria Grid Reinforcement RIT-T,PSCR) | $0.764M (transformer only) | 50% | 2028/29 |  |  |  | Refer transmission line segment data sheet |  |  |  | 22kA (500kV) 36kA (220kV) |  | $35,780/MWh | Refer Eastern Victoria Grid Reinforcement RIT-T,PSCR
| Monitored | South Morang Terminal Station | Increased demand in Metropolitan Melbourne and increased imports from NSW. | Replacement | 37.644⁰ S 145.078⁰ E | [7 empty] | 330/220kV |  |  | Replace the existing H1 transformer with a higher rated unit in conjunction with AusNet Service’s asset replacement program. | $156M (includes H1 and H2 replacement, AusNet RIT-T) |  |  | 2028 (AusNet RIT-T) | Not applicable | [6 empty] | 29kA (330kV) 24kA (220kV)
South West Victoria corridor | Monitored | Moorabool Terminal Station | New generation connected to western Victoria area and to relieve congestion. | Augmentation | 38.037⁰ S 144.296⁰ E | [7 empty] | 500/220kV |  |  | Install a third 500/220kV transformer at Moorabool Terminal Station | Unavailable | [10 empty] | 21kA (500kV) 34kA (220kV)
Northern corridor | Monitored | Dederang Terminal Station | Increased import from NSW and Murray generation (with Dederang Bus Splitter Scheme transformer control scheme active). | Augmentation | 36.454⁰ S 146.991⁰ E | [7 empty] | 330/220kV |  |  | Install a fourth 330/220 kV transformer at Dederang Terminal Station | Unavailable | [10 empty] | 20kA (330kV) 22kA (220kV)
| Priority | Wodonga Terminal Station | To enable the connection of additional renewable generation in the WOTS area. | Augmentation | 36.155⁰ S 146.95⁰ E | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | See "Wodonga MD forecast" tab | Unavailable from TCPR | Unavailable from TCPR | Unavailable from TCPR | 330/66/22 kV | Unavailable from TCPR | Unavailable from TCPR | The RIT-T PACR published in December 2024 identifies the installation of the WOTS spare transformer (330/66/22 kV 75 MVA) and a new 66kV line, as part of a suite of works to enable the connection of additional renewable generation to the WOTS sub-transmission system. | $80.4M (2024 AusNet RIT-T) | Unavailable from TCPR | Unavailable from TCPR | 2026/27 | Unavailable from TCPR | Unavailable from TCPR | 1 MVA | Unavailable from TCPR | 150MVA N rating for embedded generation export | Unavailable from TCPR | Unavailable from TCPR | 9kA (66kV) 12kA (22kV) | $0.07M in 2034 | $49,954 /MWh | 1.4 MWh in 2034
Eastern corridor |  | Hazelwood Terminal Station |  |  | 38.281⁰ S 146.428⁰ E | [7 empty] | 500kV | [14 empty] | 29kA
|  | Hazelwood Power Station |  |  | 38.273⁰ S 146.392⁰ E | [7 empty] | 220kV | [14 empty] | 36kA
|  | Jeeralang Terminal Station |  |  | 38.277⁰ S 146.424⁰ E | [7 empty] | 220kV | [14 empty] | 36kA
|  | Loy Yang Power Station |  |  | 38.256⁰ S 146.574⁰ E | [7 empty] | 500kV | [14 empty] | 29kA
|  | Morwell Terminal Station |  |  | 38.257⁰ S 146.421⁰ E | [7 empty] | 66kV | [14 empty] | 22kA
|  | Yallourn Power Station |  |  | 38.174⁰ S 146.35⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
Northern corridor |  | Wodonga Terminal Station |  |  | 36.155⁰ S 146.95⁰ E | [7 empty] | 330kV | [14 empty] | 12kA
|  | Mt Beauty Terminal Station |  |  | 36.743⁰ S 147.165⁰ E | [7 empty] | 220kV | [14 empty] | 16kA
|  | Eildon Terminal Station |  |  | 37.224⁰ S 145.921⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Dartmouth Terminal Station |  |  | 36.556⁰ S 147.521⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Mckay Creek Terminal Station |  |  | 36.858⁰ S 147.235⁰ E | [7 empty] | 220kV | [14 empty] | 11kA
|  | West Kiewa Power Station |  |  | 36.759⁰ S 147.186⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Bogong Terminal Station |  |  | 36.805⁰ S 147.229⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Greater Melbourne & Geelong |  | Plumpton Renewable Terminal Station |  |  | 37.674⁰ S 144.734⁰ E | [7 empty] | 500kV | [14 empty] | 25kA
|  | Sydenham Terminal Station |  |  | 37.676⁰ S 144.747⁰ E | [7 empty] | 500kV | [14 empty] | 25kA
|  | East Rowville Terminal Station |  |  | 37.941⁰ S 145.236⁰ E | [7 empty] | 220kV | [14 empty] | 33kA
|  | Tyabb Terminal Station |  |  | 38.268⁰ S 145.201⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Western Port Terminal Station - John Lysaght (JLA) |  |  | 38.283⁰ S 145.208⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Malvern Terminal Station |  |  | 37.878⁰ S 145.084⁰ E | [7 empty] | 220kV | [14 empty] | 17kA
|  | Springvale Terminal Station |  |  | 37.928⁰ S 145.146⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Heatherton Terminal Station |  |  | 37.941⁰ S 145.078⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Ringwood Terminal Station |  |  | 37.821⁰ S 145.216⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Templestowe Terminal Station |  |  | 37.748⁰ S 145.171⁰ E | [7 empty] | 220kV | [14 empty] | 22kA
|  | Thomastown Terminal Station |  |  | 37.693⁰ S 145.01⁰ E | [7 empty] | 220kV | [14 empty] | 30kA
|  | Richmond Terminal Station |  |  | 37.831⁰ S 145.002⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Brunswick Terminal Station |  |  | 37.773⁰ S 144.985⁰ E | [7 empty] | 220kV | [14 empty] | 30kA
|  | West Melbourne Terminal Station |  |  | 37.8⁰ S 144.935⁰ E | [7 empty] | 220kV | [14 empty] | 28kA
|  | Fishermans Bend Terminal Station |  |  | 37.825⁰ S 144.929⁰ E | [7 empty] | 220kV | [14 empty] | 27kA
|  | Newport Terminal Station |  |  | 37.841⁰ S 144.894⁰ E | [7 empty] | 220kV | [14 empty] | 24kA
|  | Laverton North Power Station |  |  | 37.842⁰ S 144.789⁰ E | [7 empty] | 220kV | [14 empty] | 23kA
|  | Geelong Terminal Station |  |  | 38.083⁰ S 144.339⁰ E | [7 empty] | 220kV | [14 empty] | 29kA
Central North corridor |  | Fosterville Terminal Station |  |  | 36.738⁰ S 144.511⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Glenrowan Terminal Station |  |  | 36.494⁰ S 146.132⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
|  | Goorambat East Terminal Station |  |  | 36.427⁰ S 145.926⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Pine Lodge Terminal Station |  |  | 36.341⁰ S 145.570⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Shepparton Terminal Station |  |  | 36.343⁰ S 145.415⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
Murray River corridor |  | Bendigo Terminal Station |  |  | 36.784⁰ S 144.254⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Carwarp Terminal Station |  |  | 34.499⁰ S 142.235⁰ E | [7 empty] | 220kV | [14 empty] | 10kA
|  | Kerang Terminal Station |  |  | 35.771⁰ S 143.934⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
|  | Kiamal Terminal Station |  |  | 35.030⁰ S 142.294⁰ E | [7 empty] | 220kV | [14 empty] | 9kA
|  | Koorangie Terminal Station |  |  | 35.730⁰ S 143.753⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Red Cliffs Terminal Station |  |  | 34.292⁰ S 142.239⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Wemen Terminal Station |  |  | 34.787⁰ S 142.524⁰ E | [7 empty] | 220kV | [14 empty] | 6kA
South West Victoria corridor |  | Heywood Terminal Station |  |  | 38.181⁰ S 141.639⁰ E | [7 empty] | 500kV | [14 empty] | 11kA
|  | Berrybank Terminal Station |  |  | 37.886⁰ S 143.453⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Blue Gum Substation |  |  | 38.061⁰ S 142.677⁰ E | [7 empty] | 500kV | [14 empty] | 14kA
|  | Cressy Terminal Station |  |  | 37.999⁰ S 143.752⁰ E | [7 empty] | 500kV | [14 empty] | 18kA
|  | Gnarwarre Terminal Station |  |  | 38.147⁰ S 144.127⁰ E | [7 empty] | 220kV | [14 empty] | 14kA
|  | Golden Plains Terminal Station |  |  | 37.972⁰ S 143.777⁰ E | [7 empty] | 220kV | [14 empty] | 20kA
|  | Haunted Gully Terminal Station |  |  | 38.008⁰ S 143.313⁰ E | [7 empty] | 500kV | [14 empty] | 14kA
|  | Mortlake Terminal Station |  |  | 38.062⁰ S 142.67⁰ E | [7 empty] | 500kV | [14 empty] | 14kA
|  | Portland Substation |  |  | 38.387⁰ S 141.631⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Tarrone Terminal Station |  |  | 38.179⁰ S 142.181⁰ E | [7 empty] | 500kV | [14 empty] | 10kA
|  | Terang Terminal Station |  |  | 38.233⁰ S 142.932⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
Western Victoria corridor |  | Ararat Terminal Station |  |  | 37.164⁰ S 143.245⁰ E | [7 empty] | 220kV | [14 empty] | 13kA
|  | Ballarat Terminal Station |  |  | 37.567⁰ S 143.921⁰ E | [7 empty] | 220kV | [14 empty] | 19kA
|  | Bulgana Terminal Station |  |  | 37.037⁰ S 142.984⁰ E | [7 empty] | 220kV | [14 empty] | 18kA
|  | Crowlands Terminal Station |  |  | 37.121⁰ S 143.154⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
|  | Elaine Terminal Station |  |  | 37.730⁰ S 144.012⁰ E | [7 empty] | 220kV | [14 empty] | 20kA
|  | Horsham Terminal Station |  |  | 36.722⁰ S 142.248⁰ E | [7 empty] | 220kV | [14 empty] | 7kA
|  | Murra Warra Terminal Station |  |  | 36.433⁰ S 142.320⁰ E | [7 empty] | 220kV | [14 empty] | 8kA
|  | Waubra Terminal Station |  |  | 37.356⁰ S 143.606⁰ E | [7 empty] | 220kV | [14 empty] | 12kA
Maximum fault levels are the maximum of three phase and single phase to ground fault levels, at the low voltage side of constrained transformers, for the next 5 years, taken from AEMO's Annual Fault Level Review report.
Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
Annual expected unserved energy is the weighted average of 10th (30% weight) and 50th (70% weight) percentile expected unserved energies.
[14 empty] | 10pcl | $M

## Altona_Brooklyn MD forecast
Station: ATS/BLTS
Import | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 292.9 | 337.3 | 385.9 | 438.5 | 455.7 | 473.5 | 492.1 | 512.1 | 532.4 | 551.3
50th percentile Winter Maximum Demand (MVA) | 295.2 | 346.5 | 397.1 | 438.8 | 451.9 | 467.3 | 483.6 | 500.9 | 518 | 533.5
10th percentile Summer Maximum Demand (MVA) | 318.7 | 363.3 | 413.1 | 465.3 | 481.4 | 499.6 | 518.5 | 538.8 | 559.1 | 578.3
10th percentile Winter Maximum Demand (MVA) | 310.4 | 362.4 | 413.6 | 455.3 | 468.4 | 484.2 | 500.7 | 518.3 | 535.7 | 551.2

## Altona West MD forecast
Station: ATS West
Import | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 247.7 | 271 | 287 | 378 | 529.4 | 635.2 | 669.1 | 678.2 | 688.6 | 694.5
50th percentile Winter Maximum Demand (MVA) | 191.4 | 220.1 | 258.2 | 386.2 | 526.6 | 588.9 | 604.2 | 612.5 | 619.8 | 624.5
10th percentile Summer Maximum Demand (MVA) | 275.1 | 299.1 | 313.7 | 408.2 | 560 | 663.5 | 698.1 | 707.8 | 718.1 | 724.7
10th percentile Winter Maximum Demand (MVA) | 201.1 | 230 | 265.9 | 394.7 | 535 | 597.9 | 613 | 621.3 | 629.8 | 634.6

## Cranbourne MD forecast
Station: CBTS 66 kV
Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 485.9 | 498.1 | 510.8 | 525.4 | 539.9 | 553.7 | 568.6 | 585.1 | 602.2 | 617.1
50th percentile Winter Maximum Demand (MVA) | 422.3 | 438 | 455.5 | 472.1 | 488 | 503.5 | 520.7 | 539.1 | 556.7 | 573.1
10th percentile Summer Maximum Demand (MVA) | 539 | 553.8 | 569.2 | 586.1 | 602.2 | 617.7 | 634.6 | 653.2 | 672.2 | 689.4
10th percentile Winter Maximum Demand (MVA) | 450.9 | 466.8 | 484.8 | 502.4 | 520.1 | 536.4 | 554.7 | 574 | 593 | 609.8

## Deer Park MD forecast
Station: DPTS 66 kV
Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 282.4 | 326.8 | 420.6 | 472.1 | 520.2 | 555.7 | 573.8 | 588.2 | 604.3 | 615.5
50th percentile Winter Maximum Demand (MVA) | 254.2 | 326.2 | 392 | 443.9 | 484.4 | 511.8 | 525 | 539 | 553.1 | 562.6
10th percentile Summer Maximum Demand (MVA) | 319.3 | 364.8 | 464.4 | 516.9 | 565.8 | 601.4 | 621.2 | 636.6 | 654.4 | 666.7
10th percentile Winter Maximum Demand (MVA) | 277.6 | 349.3 | 420.8 | 474.4 | 516.2 | 545.4 | 560 | 575.3 | 592 | 602.3

## Keilor (B1,2,5) MD forecast
Station: KTS 66 kV (B1,2,5 transformer group)
Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 339.1 | 397.7 | 469.6 | 556.5 | 621 | 667.8 | 706.2 | 742.7 | 762.5 | 781.2
50th percentile Winter Maximum Demand (MVA) | 276 | 335 | 402.2 | 479.9 | 539.2 | 581.7 | 615.4 | 646.9 | 665 | 682.4
10th percentile Summer Maximum Demand (MVA) | 366.7 | 424.2 | 496.5 | 583.2 | 647.9 | 695.1 | 734.1 | 771 | 791.3 | 810.3
10th percentile Winter Maximum Demand (MVA) | 288.1 | 347.2 | 414.3 | 492.3 | 551.9 | 594.6 | 628.6 | 660.3 | 678.6 | 696.6

## South Morang MD forecast
Station: SMTS 66 kV
Year | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 375 | 393.8 | 418.1 | 440.6 | 461.4 | 485.1 | 510.6 | 537.2 | 561.4 | 585.1
50th percentile Winter Maximum Demand (MVA) | 359.6 | 385.8 | 418 | 445.5 | 471.4 | 499.2 | 528.8 | 558.7 | 585.5 | 611.8
10th percentile Summer Maximum Demand (MVA) | 404.9 | 425.5 | 452.7 | 477.8 | 500.8 | 526.7 | 554.5 | 583.3 | 610.3 | 636.2
10th percentile Winter Maximum Demand (MVA) | 378.7 | 405.8 | 439 | 467.5 | 493.9 | 522.2 | 552.7 | 583.6 | 611.3 | 638.6

## Wodonga MD forecast
Station: WOTS 66 kV and 22 kV
Import | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
50th percentile Summer Maximum Demand (MVA) | 83.2 | 84.4 | 85.7 | 87.1 | 88.6 | 90.2 | 91.7 | 93.4 | 95.1 | 96.9
50th percentile Winter Maximum Demand (MVA) | 76.5 | 78.3 | 80.4 | 82.4 | 84.4 | 86.3 | 88.4 | 90.5 | 92.6 | 94.8
10th percentile Summer Maximum Demand (MVA) | 88.7 | 90.2 | 91.8 | 93.5 | 95.3 | 97.1 | 99 | 101 | 103 | 105.1
10th percentile Winter Maximum Demand (MVA) | 83.8 | 85.6 | 87.9 | 90.1 | 92.3 | 94.3 | 96.4 | 98.6 | 100.7 | 102.9