## Introduction
Victorian Declared Shared Network rating and loading information
This workbook presents declared shared network (DSN) rating1 and loading information at the time of the maximum demand snapshot presented in Chapter 4 of the 2025 Victorian Network Performance and Insight Report (VNPIR).
The "Maximum demand 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the maximum demand snapshot.
The "Maximum demand 2" worksheet presents a summary of Interconnector power flows and limits at the time of the maximum demand snapshot.
The "High export to NSW 1" worksheet presents the continuous and short-term line and transformer ratings, as well as (N) and (N-1) loadings at the time of the high power flow from Victoria to NSW snapshot. Only Northern Corridor elements elements (together with South Morang transformers) are shown for this snapshot as this is the only region where DSN elements tend to be more heavily loaded during high export from Victoria, rather than during high Victorian demand.
The "High export to NSW 2" worksheet presents a summary of the reactive power adequacy, as well as Interconnector power flows and limits at the time of the high power flow from Victoria to NSW snapshot.
The (N) loading for an asset presents its % loading under system normal condition, based on the asset’s continuous rating.
The (N-1) loading of an asset presents its % loading following the worst single credible contingency, based on the asset’s short term rating. The reported short-term ratings for transmission lines represent the 15 minute ratings.
Rating types are shown in the tables as “D” (dynamic rating), “D/W” (dynamic rating with wind monitoring), and “S” (static rating).
Dynamic ratings (D) are used in real time by AEMO system operators, calculated by taking into account the ambient temperature and a solar heating factor calculation based on the date and time. For lines equipped with wind monitoring facilities (D/W), the calculation of dynamic ratings also takes into account the actual wind speed, otherwise a standard wind speed of 0.6 m/s is assumed.
The rating for equipment with static ratings (S) is based on ambient temperatures that assume a wind speed of 0.6 m/s. Short-term ratings are not available for some lines with static ratings, in which case, the short-term rating is equal to the continuous rating.
[1] AEMO. AEMO transmission equipment ratings. Available at https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/data-nem/network-data/transmission-equipment-ratings

## Maximum demand 1
Table 1 — Maximum demand snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MW) | Continuous loading (N) MVAr | Continuous loading (N) (MVA) | Short–term rating* (N–1) (MVA) | Short-term loading (N-1) (MW) | Short-term loading (N-1) (MVAr) | Short-term loading (N-1) (MVA) | Rating type | (N) loading | (N–1) loading | Critical contingency
Eastern Corridor | 500 kV | Hazelwood 500kV - Loy Yang 500kV 1 | 3031 | 995.3754 | 64.8259 | 997.4841 | 3031 | 1492.978 | 87.4556 | 1496 | D | 32.91% | 49.36% | Hazelwood 500kV - Loy Yang 500kV 2
|  | Hazelwood 500kV - Loy Yang 500kV 2 | 3215 | 982.0369 | 63.3072 | 984.0753 | 3464 | 1483.0386 | 86.2593 | 1486 | D | 30.61% | 42.9% | Hazelwood 500kV - Loy Yang 500kV 1
|  | Hazelwood 500kV - Loy Yang 500kV 3 | 3215 | 969.0494 | 61.813 | 971.0189 | 3464 | 1463.421 | 84.0166 | 1466 | D | 30.2% | 42.32% | Hazelwood 500kV - Loy Yang 500kV 1
|  | Hazelwood 500kV - South Morang 500kV 1 | 2858 | 666.9683 | 89.4776 | 672.9435 | 2858 | 935.3882 | 71.6299 | 938 | S | 23.55% | 32.82% | Cranbourne 500kV - Hazelwood 500kV 1
|  | Hazelwood 500kV - South Morang 500kV 2 | 2858 | 667.3847 | 89.5047 | 673.3598 | 2858 | 935.9728 | 71.658 | 939 | S | 23.56% | 32.86% | Cranbourne 500kV - Hazelwood 500kV 1
|  | Hazelwood 500kV - Rowville 500kV | 3447 | 858.3307 | 77.3599 | 861.8099 | 3447 | 1286.8333 | 37.8047 | 1287 | S | 25% | 37.34% | Cranbourne 500kV - Hazelwood 500kV 1
|  | Cranbourne 500kV - Hazelwood 500kV | 3447 | 965.5367 | 67.9231 | 967.9228 | 3447 | 1350.7122 | 33.7124 | 1351 | S | 28.08% | 39.19% | Hazelwood 500kV - Rowville 500kV 1
| 220 kV | Rowville 220kV - Yallourn 220kV 1 | 305 | 92.0054 | 6.8855 | 92.2627 | 336 | 137.9208 | 10.3676 | 138 | D/W | 30.25% | 41.07% | Hazelwood 220kV - Yallourn 220kV 1
|  | Rowville 220kV - Yallourn 220kV 2 | 305 | 128.3447 | 2.1177 | 128.3622 | 336 | 179.8641 | 12.9779 | 180 | D/W | 42.09% | 53.57% | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Yallourn 220kV 3 | 305 | 130.9437 | 1.9479 | 130.9582 | 336 | 183.5176 | 12.9406 | 184 | D/W | 42.94% | 54.76% | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Yallourn 220kV 4 | 305 | 130.9437 | 1.9479 | 130.9582 | 336 | 183.5176 | 12.9406 | 184 | D/W | 42.94% | 54.76% | Rowville 500/220kV A1 Transformer
|  | Hazelwood 220kV - Yallourn 220kV 1 | 413 | 142.1985 | 14.262 | 142.912 | 458 | 185.5699 | 22.1475 | 187 | D | 34.6% | 40.83% | Rowville 500/220kV A2 Transformer
|  | Hazelwood 220kV - Yallourn 220kV 2 | 413 | 308.7408 | 44.3029 | 311.9032 | 527 | 308.7418 | 33.6775 | 311 | D | 75.52% | 59.01% | Cranbourne 500kV - Hazelwood 500kV
|  | Hazelwood 220kV - Rowville 220kV 1 | 307 | 70.9003 | 7.1738 | 71.2623 | 334 | 92.7038 | 8.3937 | 93 | D/W | 23.21% | 27.84% | Hazelwood 220kV - Rowville 220kV 2
|  | Hazelwood 220kV - Rowville 220kV 2 | 307 | 70.9798 | 7.1533 | 71.3394 | 334 | 92.7755 | 8.3798 | 93 | D/W | 23.24% | 27.84% | Hazelwood 220kV - Rowville 220kV 1
|  | Hazelwood 220kV - Morwell 220kV | 314 | 91.9468 | 18.7387 | 93.8368 | 395 | 149.989 | 43.6657 | 156 | S | 29.88% | 39.49% | Jeeralang 220kV - Morwell 220kV 1
|  | Jeeralang 220kV - Morwell 220kV 1 | 400 | 111.3744 | 13.5308 | 112.1933 | 400 | 178.3642 | 43.9709 | 184 | S | 28.05% | 46% | Morwell 220/66kV B2 Transformer
|  | Jeeralang 220kV - Morwell 220kV 2 | 400 | 109.0617 | 15.5344 | 110.1625 | 400 | 167.9465 | 40.831 | 173 | S | 27.54% | 43.25% | Jeeralang 220kV - Morwell 220kV 1
|  | Hazelwood 220kV - Jeeralang 220kV 1 | 799 | 0.97147 | 17.0352 | 17.0629 | 799 | 25.2418 | 26.9295 | 37 | D | 2.136% | 4.631% | Hazelwood 220kV - Morwell 220kV 1
|  | Hazelwood 220kV - Jeeralang 220kV 2 | 799 | 0.98424 | 16.655 | 16.6841 | 799 | 24.6308 | 26.4464 | 36 | D | 2.088% | 4.506% | Hazelwood 220kV - Morwell 220kV 1
|  | Hazelwood 220kV - Jeeralang 220kV 3 | 413 | 0.31708 | 13.9108 | 13.9144 | 454 | 21.47 | 21.3263 | 30 | D | 3.369% | 6.608% | Morwell 220/66kV B3 Transformer
|  | Hazelwood 220kV - Jeeralang 220kV 4 | 413 | 0.31708 | 13.9108 | 13.9144 | 431 | 21.47 | 21.3263 | 30 | D | 3.369% | 6.961% | Morwell 220/66kV B3 Transformer
| 500/220 kV | Rowville 500/220kV A1 Transformer | 1000 | 826.8 | 91.4 | 831.8366 | 1500 | 971.2 | 179.7 | 988 | S | 83.18% | 65.87% | Ringwood 220kV- Thomastown 200kV 1
|  | Rowville 500/220kV A2 Transformer | 1000 | 650.9 | 105.2 | 659.3465 | 1500 | 982.3 | 62.8 | 984 | S | 65.93% | 65.6% | Cranbourne 500/220kV A1 Transformer
|  | Hazelwood 500/220kV A1 Transformer | 600 | 53.2 | 36 | 64.2358 | 638 | 71 | 44.5 | 84 | S | 10.71% | 13.17% | Hazelwood 500/220kV A3 Transformer
|  | Hazelwood 500/220kV A2 Transformer | 600 | 53.7 | 36.4 | 64.8741 | 638 | 71.7 | 45 | 85 | S | 10.81% | 13.32% | Hazelwood 500/220kV A3 Transformer
|  | Hazelwood 500/220kV A3 Transformer | 600 | 53.9 | 36.5 | 65.0958 | 638 | 71.9 | 45.1 | 85 | S | 10.85% | 13.32% | Hazelwood 500/220kV A2 Transformer
|  | Hazelwood 500/220kV A4 Transformer | 600 | 53.7 | 36.4 | 64.8741 | 638 | 71.7 | 45 | 85 | S | 10.81% | 13.32% | Hazelwood 500/220kV A3 Transformer
South–West Corridor | 500 kV | Heywood 500kV - Tarrone 500kV | 2771 | 52.5945 | 129.2603 | 139.5508 | 2771 | 764.8556 | 102.2757 | 772 | S | 5.036% | 27.86% | Cressy 500kV - Mortlake 500kV
|  | Haunted Gully 500kV - Cressy 500kV | 2858 | 456.3201 | 60.7282 | 460.3433 | 2858 | 1265.427 | 94.5627 | 1269 | S | 16.11% | 44.4% | Cressy 500kV - Mortlake 500kV
|  | Cressy 500kV - Moorabool 500kV 1 | 2858 | 491.9427 | 14.7317 | 492.1633 | 2858 | 1267.675 | 59.7812 | 1269 | S | 17.22% | 44.4% | Cressy 500kV - Moorabool 500kV 2
|  | Cressy 500kV - Moorabool 500kV 2 | 2858 | 477.0408 | 15.9487 | 477.3073 | 2858 | 1267.6666 | 59.738 | 1269 | S | 16.7% | 44.4% | Cressy 500kV - Moorabool 500kV 1
|  | Haunted Gully 500kV - Tarrone 500kV | 2858 | 134.1471 | 67.0483 | 149.9698 | 2858 | 949.4464 | 44.85 | 951 | S | 5.247% | 33.28% | Cressy 500kV - Mortlake 500kV
|  | Cressy 500kV - Mortlake 500kV | 2598 | 477.0408 | 15.9487 | 477.3073 | 2598 | 1267.6666 | 59.738 | 1269 | S | 18.37% | 48.85% | Cressy 500kV - Moorabool 500kV 1
|  | Heywood 500kV - Mortlake 500kV | 2771 | 210.2976 | 56.8058 | 217.8348 | 2771 | 728.4966 | 54.2533 | 731 | S | 7.861% | 26.38% | Cressy 500kV - Mortlake 500kV
|  | Alcoa Portland 500kV - Heywood 500kV 1 | 1386 | 148.6911 | 191.4204 | 242.3857 | 1386 | 296.02 | 272.2615 | 402 | S | 17.49% | 29% | Alcoa Portland 500kV - Alcoa Portland 500kV 2
|  | Alcoa Portland 500kV - Heywood 500kV 2 | 1386 | 147.7913 | 190.3237 | 240.9676 | 1386 | 296.0092 | 272.2178 | 402 | S | 17.39% | 29% | Alcoa Portland 500kV - Alcoa Portland 500kV 1
| 275 kV | South East 275kV - Heywood 275kV 1 | 617 | 17 | 49 | 51.8652 | 717 | 34.1 | 61.9 | 71 | D | 8.406% | 9.902% | Heywood 275kV - South East 275kV 2
|  | South East 275kV - Heywood 275kV 2 | 617 | 17 | 49 | 51.8652 | 717 | 34.1 | 61.9 | 71 | D | 8.406% | 9.902% | Heywood 275kV - South East 275kV 1
| 500/275 kV | Heywood 500/275kV M1 Transformer | 300 | 11 | 43 | 44.3847 | 525 | 16.9476 | 61.9907 | 64 | S | 14.79% | 12.19% | Heywood 500/275kV M2 Transformer
|  | Heywood 500/275kV M2 Transformer | 300 | 11 | 42 | 43.4166 | 525 | 16.9476 | 61.9907 | 64 | S | 14.47% | 12.19% | Heywood 500/275kV M1 Transformer
|  | Heywood 500/275kV M3 Transformer | 370 | 11 | 42 | 43.4166 | 525 | 16.9476 | 61.9907 | 64 | S | 11.73% | 12.19% | Heywood 500/275kV M1 Transformer
Northern Corridor | 330 kV | Dederang 330kV - Wodonga 330kV | 743 | 274.2211 | 75.6437 | 284.4629 | 743 | 416.2 | 74.35 | 423 | D | 38.29% | 56.93% | Loy Yang B2 generating unit
|  | Dederang 330kV - Murray 330kV 1 | 1043 | 237.8757 | 82.6391 | 251.8215 | 1124 | 457.4721 | 58.5619 | 461 | D | 24.14% | 41.01% | Loy Yang B2 generating unit
|  | Dederang 330kV - Murray 330kV 2 | 1043 | 234.8428 | 84.9134 | 249.7227 | 1124 | 452.5922 | 63.7078 | 457 | D | 23.94% | 40.66% | Loy Yang B2 generating unit
|  | Dederang 330kV - South Morang 330kV 1 | 943 | 335.095 | 103.4968 | 350.7139 | 1086 | 551.7624 | 251.317 | 606 | D | 37.19% | 55.8% | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330kV - South Morang 330kV 2 | 943 | 334.2189 | 103.1067 | 349.7618 | 1086 | 551.3405 | 250.8393 | 606 | D | 37.09% | 55.8% | Dederang 330kV - South Morang 330kV 1
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 271 | 125.5461 | 39.3777 | 131.5767 | 271 | 307.1531 | 42.699 | 310 | D | 48.55% | 114.4% | Eildon 220kV - Thomastown 220kV
|  | Dederang 220kV - Mount Beauty 220kV 2 | 271 | 125.5461 | 39.3777 | 131.5767 | 271 | 307.1531 | 42.699 | 310 | D | 48.55% | 114.4% | Eildon 220kV - Thomastown 220kV
|  | Dartmouth 220kV - Mount Beauty 220kV | 230 | 166.5967 | 11.586 | 166.9991 | 230 | 16.6597 | 1.2664 | 17 | D | 72.61% | 7.391% | Bogong 220kV - McKAY 220kV
|  | Bogong 220kV - Mount Beauty 220kV | 840 | 150.678 | 16.7789 | 151.6093 | 840 | 75.3391 | 8.3137 | 76 | D | 18.05% | 9.048% | Rowville 500/220kV A1 Transformer
|  | Mount Beauty 220kV - West Kiewa 220kV | 97 | 61.085 | 9.0437 | 61.7508 | 97 | 5.5532 | 0.66475 | 6 | S | 63.66% | 6.186% | Dederang 220kV - Mount Beauty 220kV 1
|  | Eildon 220kV - Thomastown 220kV | 541 | 362.8801 | 5.1855 | 362.9171 | 541 | 433.9548 | 13.0109 | 434 | D | 67.08% | 80.22% | Loy Yang B2 generating unit
|  | Eildon 220kV - Mount Beauty 220kV 1 | 271 | 124.7298 | 7.7196 | 124.9685 | 271 | 179.9459 | 14.321 | 181 | D | 46.11% | 66.79% | Eildon 220kV - Mount Beauty 220kV 2
|  | Eildon 220kV - Mount Beauty 220kV 2 | 271 | 124.7298 | 7.7196 | 124.9685 | 271 | 179.9459 | 14.321 | 181 | D | 46.11% | 66.79% | Eildon 220kV - Mount Beauty 220kV 1
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 26 | 9.3 | 27.6132 | 400 | 109.6097 | 9.2998 | 110 | S | 8.122% | 27.5% | Eildon 220kV - Thomastown 220kV
|  | Dederang 330/220kV H2 Transformer | 340 | 23.1 | 8.2 | 24.5122 | 400 | 97.4364 | 8.1852 | 98 | S | 7.209% | 24.5% | Eildon 220kV - Thomastown 220kV
|  | Dederang 330/220kV H3 Transformer | 240 | 22.4 | 6.6 | 23.3521 | 240 | 92.3229 | 6.619 | 93 | S | 9.73% | 38.75% | Eildon 220kV - Thomastown 220kV
Greater Melbourne and Geelong | 500 kV | Moorabool 500kV - Sydenham 500kV 1 | 2598 | 249.0872 | 94.1829 | 266.2984 | 2598 | 460.5052 | 119.5687 | 476 | S | 10.25% | 18.32% | Moorabool 500kV - Sydenham 500kV 2
|  | Moorabool 500kV - Sydenham 500kV 2 | 2598 | 249.0872 | 94.1991 | 266.3042 | 2598 | 460.5051 | 119.5852 | 476 | S | 10.25% | 18.32% | Moorabool 500kV - Sydenham 500kV 1
|  | Keilor 500kV - Sydenham 500kV | 1949 | 709.1362 | 187.6035 | 733.5321 | 1949 | 1107.0828 | 218.3238 | 1128 | S | 37.64% | 57.88% | Keilor 500kV - South Morang 500kV
|  | Keilor 500kV - South Morang 500kV | 2598 | 447.7545 | 45.9601 | 450.1071 | 2598 | 1044.2925 | 184.5049 | 1060 | S | 17.33% | 40.8% | Keilor 500kV - Sydenham 500kV
|  | South Morang 500kV - Sydenham 500kV 1 | 2598 | 106.5322 | 54.1275 | 119.4944 | 2598 | 308.5789 | 40.5083 | 311 | S | 4.599% | 11.97% | Keilor 500kV - South Morang 500kV
|  | South Morang 500kV - Sydenham 500kV 2 | 2651 | 104.8948 | 54.0489 | 118.0009 | 2651 | 303.7633 | 40.4284 | 306 | S | 4.451% | 11.54% | Keilor 500kV - South Morang 500kV
|  | Rowville 500kV - South Morang 500kV | 3447 | 364.9331 | 48.5213 | 368.1447 | 3447 | 809.5649 | 54.1748 | 811 | S | 10.68% | 23.53% | Hazelwood 500kV - Cranbourne 500kV
|  | Cranbourne 500kV - Rowville 500kV | 2771 | 261.5424 | 19.2554 | 262.2503 | 2771 | 860.7887 | 2.8906 | 861 | S | 9.464% | 31.07% | Cranbourne 500/220kV A1 Transformer
| 220 kV | Geelong 220kV - Moorabool 220kV 1 | 800 | 372.8996 | 27.8387 | 373.9373 | 800 | 708.9495 | 59.6617 | 711 | D | 46.74% | 88.88% | Geelong 220kV - Moorabool 220kV 2
|  | Geelong 220kV - Moorabool 220kV 2 | 819 | 372.8996 | 27.8387 | 373.9373 | 819 | 708.9495 | 59.6617 | 711 | D | 45.66% | 86.81% | Geelong 220kV - Moorabool 220kV 1
|  | Geelong 220kV - Keilor 220kV 1 | 271 | 120.4524 | 8.5648 | 120.7565 | 271 | 161.8934 | 2.9825 | 162 | D/W | 44.56% | 59.78% | Deer Park 220kV - Geelong 220kV
|  | Deer Park 220kV - Geelong 220kV 2 | 271 | 172.8432 | 15.6831 | 173.5532 | 271 | 323.1224 | 205.2268 | 383 | D/W | 64.04% | 141.3% | Deer Park 220kV - Keilor 220kV
|  | Deer Park 220kV - Keilor 220kV 2 | 271 | 141.2847 | 101.5517 | 173.9945 | 271 | 313.231 | 122.9522 | 336 | D/W | 64.2% | 124% | Deer Park 220kV - Geelong 220kV
|  | Geelong 220kV - Keilor 220kV 3 | 271 | 120.5431 | 8.5555 | 120.8463 | 271 | 162.0155 | 2.9665 | 162 | D/W | 44.59% | 59.78% | Deer Park 220kV - Geelong 220kV
|  | Altona 220kV - Keilor 220kV | 827 | 142.9557 | 26.3475 | 145.3635 | 1006 | 277.4902 | 68.4173 | 286 | D | 17.58% | 28.43% | Brooklyn 220kV - Keilor 220kV 1
|  | Brooklyn 220kV - Keilor 220kV | 827 | 176.4161 | 51.9463 | 183.905 | 962 | 374.582 | 74.444 | 382 | D | 22.24% | 39.71% | Altona 220kV - Keilor 220kV 1
|  | Altona 220kV - Brooklyn 220kV | 827 | 74.5331 | 57.9443 | 94.4072 | 910 | 205.7322 | 96.7166 | 227 | D | 11.42% | 24.95% | Brooklyn 220kV - Keilor 220kV 1
|  | Brooklyn 220kV - Newport 220kV | 800 | 7.0566 | 1.4595 | 7.2059 | 800 | 363.1129 | 57.7338 | 368 | D | 0.9007% | 46% | Fishermans Bend 220kV - Newport 220kV 1
|  | Brooklyn 220kV - Fishermans Bend 220kV | 823 | 17.6261 | 9.6851 | 20.1117 | 823 | 170.2857 | 57.6441 | 180 | D | 2.444% | 21.87% | Fishermans Bend 220kV - Newport 220kV 1
|  | Fishermans Bend 220kV - Newport 220kV | 827 | 356.1953 | 77.7011 | 364.5718 | 827 | 416.0745 | 62.3244 | 421 | D | 44.08% | 50.91% | Keilor 500/220kV A2 Transformer
|  | Fishermans Bend 220kV - West Melbourne 220kV 1 | 400 | 87.7317 | 30.2699 | 92.8069 | 481 | 171.5052 | 58.2065 | 181 | D | 23.2% | 37.63% | Fishermans Bend 220kV - West Melbourne 220kV 2
|  | Fishermans Bend 220kV - West Melbourne 220kV 2 | 400 | 87.7317 | 30.2699 | 92.8069 | 481 | 171.5052 | 58.2065 | 181 | D | 23.2% | 37.63% | Fishermans Bend 220kV - West Melbourne 220kV 1
|  | Keilor 220kV - West Melbourne 220kV 1 | 800 | 30.045 | 22.9388 | 37.8007 | 800 | 171.5014 | 39.9274 | 176 | D | 4.725% | 22% | Newport generating unit
|  | Keilor 220kV - West Melbourne 220kV 2 | 800 | 29.9497 | 22.8556 | 37.6744 | 800 | 170.9287 | 39.7386 | 175 | D | 4.709% | 21.88% | Newport generating unit
|  | Keilor 220kV - Thomastown 220kV 1 | 613 | 204.8236 | 6.2677 | 204.9195 | 634 | 475.4991 | 27.7167 | 476 | S | 33.43% | 75.08% | South Morang 330/220kV H3 Transformer
|  | Keilor 220kV - Thomastown 220kV 2 | 674 | 171.3443 | 100.2317 | 198.5076 | 854 | 337.5854 | 62.1384 | 343 | S | 29.45% | 40.16% | Rowville 500/220kV A2 Transformer
|  | South Morang 220kV - Thomastown 220kV 1 | 629 | 353.3753 | 45.6281 | 356.3089 | 692 | 486.015 | 50.4358 | 489 | S | 56.65% | 70.66% | South Morang 220kV - Thomastown 220kV 2
|  | South Morang 220kV - Thomastown 220kV 2 | 629 | 410.4417 | 48.9661 | 413.3522 | 692 | 535.6701 | 50.4378 | 538 | S | 65.72% | 77.75% | Rowville 500/220kV A1 Transformer
|  | Brunswick 220kV - Thomastown 220kV 1 | 629 | 5.3848 | 65.4079 | 65.6292 | 736 | 247.9615 | 99.3756 | 267 | D | 10.43% | 36.28% | South Morang 220kV - Thomastown 220kV 2
|  | Brunswick 220kV - Thomastown 220kV 3 | 800 | 440.8813 | 59.0803 | 444.8223 | 917 | 590.7241 | 41.297 | 592 | D | 55.6% | 64.56% | South Morang 220kV - Thomastown 220kV 2
|  | Ringwood 220kV - Thomastown 220kV | 705 | 340.6745 | 113.8132 | 359.1832 | 705 | 687.4692 | 122.3538 | 698 | D | 50.95% | 99.01% | Rowville 500/220kV A1 Transformer
|  | Templestowe 220kV - Thomastown 220kV | 705 | 239.446 | 85.8157 | 254.3595 | 705 | 577.4201 | 89.3267 | 584 | D | 36.08% | 82.84% | Rowville 500/220kV A1 Transformer
|  | Rowville 220kV - Templestowe 220kV | 827 | 74.826 | 35.6858 | 82.9 | 861 | 314.9322 | 69.4425 | 322 | D | 10.02% | 37.4% | Templestowe 220kV - Thomastown 220kV
|  | Rowville 220kV - Thomastown 220kV | 630 | 5.8997 | 22.2723 | 23.0404 | 693 | 155.6474 | 38.7907 | 160 | D | 3.657% | 23.09% | Brunswick 220kV - Thomastown 220kV 3
|  | Ringwood 220kV - Rowville 220kV | 739 | 164.3646 | 30.1437 | 167.1058 | 739 | 504.8474 | 100.0074 | 515 | D | 22.61% | 69.69% | Ringwood 220kV - Thomastown 220kV
|  | Malvern 220kV - Rowville 220kV 1 | 271 | 113.2044 | 39.2287 | 119.8087 | 315 | 225.9502 | 83.5754 | 241 | D | 44.21% | 76.51% | Malvern 220kV - Rowville 220kV 2
|  | Malvern 220kV - Rowville 220kV 2 | 271 | 113.1954 | 39.2775 | 119.8161 | 315 | 225.9487 | 83.5753 | 241 | D | 44.21% | 76.51% | Malvern 220kV - Rowville 220kV 1
|  | Rowville 220kV - Springvale 220kV 1 | 800 | 372.0924 | 6.3312 | 372.1462 | 953 | 745.3632 | 2.6237 | 745 | D/W | 46.52% | 78.17% | Rowville 220kV - Springvale 220kV 2
|  | Rowville 220kV - Springvale 220kV 2 | 800 | 372.0924 | 6.3312 | 372.1462 | 953 | 745.3632 | 2.6237 | 745 | D/W | 46.52% | 78.17% | Rowville 220kV - Springvale 220kV 1
|  | Richmond 220kV - Rowville 220kV 1 | 630 | 197.6818 | 1.4906 | 197.6874 | 860 | 315.151 | 23.9069 | 316 | D | 31.38% | 36.74% | Thomastown 220kV - Brunswick 220kV 3
|  | Richmond 220kV - Rowville 220kV 2 | 630 | 196.4153 | 2.051 | 196.4261 | 860 | 312.2991 | 22.8571 | 313 | D | 31.18% | 36.4% | Thomastown 220kV - Brunswick 220kV 3
|  | Heatherton 220kV - Springvale 220kV 1 | 400 | 181.6069 | 8.6396 | 181.8123 | 452 | 363.0966 | 22.4842 | 364 | D | 45.45% | 80.53% | Heatherton 220kV - Springvale 220kV 2
|  | Heatherton 220kV - Springvale 220kV 2 | 400 | 181.6069 | 8.6396 | 181.8123 | 452 | 363.0966 | 22.4842 | 364 | D | 45.45% | 80.53% | Heatherton 220kV - Springvale 220kV 1
|  | East Rowville 220kV - Rowville 220kV 1 | 800 | 240.8266 | 132.1888 | 274.7204 | 879 | 590.7099 | 80.1641 | 596 | D | 34.34% | 67.8% | Cranbourne 500/220kV A1 Transformer
|  | East Rowville 220kV - Rowville 220kV 2 | 798 | 240.8266 | 132.1888 | 274.7204 | 798 | 590.7099 | 80.1641 | 596 | D | 34.43% | 74.69% | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - East Rowville 220kV 1 | 800 | 23.8252 | 123.7255 | 125.9986 | 800 | 373.5673 | 66.05 | 379 | D | 15.75% | 47.38% | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - East Rowville 220kV 2 | 800 | 23.8252 | 123.7255 | 125.9986 | 800 | 373.5673 | 66.05 | 379 | D | 15.75% | 47.38% | Cranbourne 500/220kV A1 Transformer
|  | Cranbourne 220kV - Tyabb 220kV 1 | 543 | 122.1112 | 9.219 | 122.4587 | 543 | 133.6888 | 11.4792 | 134 | D | 22.55% | 24.68% | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 2
|  | Cranbourne 220kV - Tyabb 220kV 2 | 543 | 122.1112 | 9.219 | 122.4587 | 543 | 244.806 | 36.4871 | 248 | D | 22.55% | 45.67% | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 1
|  | John Lysaght 220kV - Tyabb 220kV 1 | 183 | 9.3637 | 6.5507 | 11.4276 | 183 | 18.7259 | 13.0995 | 23 | S | 6.245% | 12.57% | John Lysaght 220kV - Tyabb 220kV 2
|  | John Lysaght 220kV - Tyabb 220kV 2 | 183 | 9.3637 | 6.5507 | 11.4276 | 183 | 18.7274 | 13.1014 | 23 | S | 6.245% | 12.57% | Cranbourne 220kV - Tyabb 220kV - John Lysaght 220kV 1
|  | Brunswick 220kV - Richmond 220kV | 450 | 54.1898 | 54.8485 | 77.1032 | 650 | 268.8451 | 27.3507 | 270 | S | 17.13% | 41.54% | Rowville 500/220kV A2 Transformer
| 500/220 kV | Keilor 500/220kV A2 Transformer | 750 | 359 | 68 | 365.3834 | 810 | 497 | 117 | 511 | S | 48.72% | 63.09% | Keilor 500/220kV A4 Transformer
|  | Keilor 500/220kV A3 Transformer | 750 | 437.2 | 97.9 | 448.0271 | 810 | 562 | 132 | 577 | S | 59.74% | 71.23% | Rowville 500/220kV A1 Transformer
|  | Keilor 500/220kV A4 Transformer | 750 | 361 | 68 | 367.3486 | 810 | 499 | 117 | 513 | S | 48.98% | 63.33% | Keilor 500/220kV A2 Transformer
|  | Cranbourne 500/220kV A1 Transformer | 1000 | 695.8685 | 105.9618 | 703.8898 | 1500 | 951 | 6 | 951 | S | 70.39% | 63.4% | Rowville 500/220kV A2 Transformer
| 500/330 kV | South Morang 500/330kV F2 Transformer | 1000 | 151.5019 | 97.4066 | 180.1135 | 1200 | 275.1507 | 124.8511 | 302 | S | 18.01% | 25.17% | Rowville 500/220kV A1Transformer
| 330/220 kV | South Morang 330/220kV H1 Transformer | 700 | 457.4 | 23.7 | 458.0136 | 850 | 585.5177 | 56.1196 | 588 | S | 65.43% | 69.18% | Rowville 500/220kV A1 Transformer
|  | South Morang 330/220kV H2 Transformer1 | 700 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | S | 0% | 0% | -
|  | South Morang 330/220kV H3 Transformer | 700 | 493.5 | 73.3 | 498.914 | 1000 | 617.9439 | 105.6157 | 627 | S | 71.27% | 62.7% | Rowville 500/220kV A1 Transformer
Regional Victoria | 220 kV | Red Cliffs 220kV - Buronga 220kV 1 | 410 | 67.7353 | 25.275 | 72.2973 | 411 | 133.8002 | 46.0887 | 142 | S | 17.63% | 34.55% | Red Cliffs 220kV - Buronga 220kV 2
|  | Kiamal 220kV - Murra Warra 220kV - Horsham | 450 | 88.8964 | 30.0867 | 93.8497 | 450 | 311.1028 | 49.0706 | 315 | D/W | 20.86% | 70% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Kiamal 220kV - Red Cliffs 220kV 1 | 450 | 100.0962 | 34.6504 | 105.9241 | 450 | 301.5962 | 58.7753 | 307 | D/W | 23.54% | 68.22% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Red Cliffs 220kV - Wemen 220kV - Kerang 220kV | 267 | 70.3006 | 49.3288 | 85.8808 | 274 | 192.6842 | 53.814 | 200 | D/W | 32.17% | 72.99% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Ballarat 220kV - Waubra 220kV - Ararat 220kV | 450 | 270.3216 | 87.3559 | 284.0859 | 450 | 343.0811 | 121.095 | 364 | D/W | 63.13% | 80.89% | Kiamal 220kV - Murra Warra KV -Horsham 220 Kv
|  | Ararat 220kV - Crowlands 220kV | 450 | 140.4467 | 54.1261 | 150.5154 | 500 | 223.1999 | 76.4647 | 236 | D/W | 33.45% | 47.2% | Kiamal 220kV - Murra Warra KV -Horsham 220 Kv
|  | Bulgana 220kV - Horsham 220kV | 450 | 37.5761 | 16.6588 | 41.1033 | 508 | 310.5191 | 38.1024 | 313 | D/W | 9.134% | 61.61% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Bulgana 220kV - Crowlands 220kV | 450 | 76.8612 | 56.8503 | 95.6013 | 506 | 196.8092 | 17.5841 | 198 | D/W | 21.24% | 39.13% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Bendigo 220kV - Kerang 220kV | 347 | 15.9569 | 20.124 | 25.6827 | 347 | 126.1329 | 43.1835 | 133 | D/W | 7.401% | 38.33% | Ararat 220kV - Waubra 220kV - Ballarat 220kV
|  | Ballarat 220kV - Bendigo 220kV | 271 | 117.1361 | 28.3634 | 120.5212 | 308 | 183.1358 | 18.4176 | 184 | D/W | 44.47% | 59.74% | Kiamal 220kV - Murra Warra KV -Horsham 220 Kv
|  | Ballarat 220kV - Berrybank 220kV | 438 | 135.6073 | 10.1813 | 135.989 | 438 | 206.1416 | 0.12825 | 206 | D/W | 31.05% | 47.03% | Moorabool 220kV - Terang 220kV 1
|  | Berrybank 220kV - Terang 220kV | 450 | 14.8872 | 14.312 | 20.6509 | 487 | 120.7884 | 13.8627 | 122 | D/W | 4.589% | 25.05% | Ballarat 220kV - Berrybank 220kV 1
|  | Ballarat 220kV - Moorabool 220kV 1 | 271 | 57.6718 | 11.3998 | 58.7877 | 271 | 84.0221 | 15.8109 | 85 | D/W | 21.69% | 31.37% | Ballarat 220kV - Moorabool 220kV 2
|  | Ballarat 220kV - Moorabool 220kV 2 | 463 | 74.8233 | 20.0633 | 77.4665 | 463 | 109.9057 | 27.2578 | 113 | D/W | 16.73% | 24.41% | Ballarat 220kV - Elaine 220kV
|  | Ballarat 220kV - Elaine 220kV | 448 | 69.8367 | 23.6187 | 73.7225 | 448 | 103 | 31 | 108 | D/W | 16.46% | 24.11% | Ballarat 220kV - Moorabool 220kV 2
|  | Elaine 220kV - Moorabool 220kV | 448 | 74.0976 | 13.4741 | 75.3127 | 448 | 107 | 22 | 109 | D/W | 16.81% | 24.33% | Ballarat 220kV - Moorabool 220kV 2
|  | Moorabool 220kV - Terang 220kV | 271 | 75.4659 | 6.3111 | 75.7293 | 314 | 200.303 | 3.4 | 200 | D/W | 27.94% | 63.69% | Ballarat 220kV - Berrybank 220kV 1
|  | Bendigo 220kV - Fosterville 220kV - Shepparton 220kV | 394.14 | 96.7 | 7.4 | 96.9827 | 480.386 | 182.3805 | 8.0854 | 183 | D/W | 24.61% | 38.09% | Ballarat 220kV - Bendigo 220kV 1
|  | Glenrowan 220kV - Shepparton 220kV 1 | 450 | 112.8426 | 6.8826 | 113.0523 | 450 | 192.7208 | 5.1176 | 193 | D | 25.12% | 42.89% | Glenrowan 220kV - Shepparton 220kV 2
|  | Glenrowan 220kV - Shepparton 220kV 2 | 450 | 112.8426 | 6.8826 | 113.0523 | 450 | 192.7208 | 5.1176 | 193 | D | 25.12% | 42.89% | Glenrowan 220kV - Shepparton 220kV 1
|  | Dederang 220kV - Shepparton 220kV | 271 | 87.8576 | 9.3398 | 88.3527 | 271 | 56.1749 | 5.7336 | 56 | D | 32.6% | 20.66% | Dederang 220kV - Glenrowan 220kV 1
|  | Dederang 220kV - Glenrowan 220kV 1 | 450 | 116.5898 | 21.7947 | 118.6094 | 450 | 193.4738 | 35.702 | 197 | D | 26.36% | 43.78% | Dederang 220kV - Glenrowan 220kV 2
|  | Dederang 220kV - Glenrowan 220kV 2 | 450 | 116.5898 | 21.7947 | 118.6094 | 482 | 193.4738 | 35.702 | 197 | D | 26.36% | 40.87% | Dederang 220kV - Glenrowan 220kV 1
| 500/220 kV | Moorabool 500/220kV A1 Transformer | 1000 | 231 | 135 | 267.5556 | 1310 | 381 | 156 | 412 | S | 26.76% | 31.45% | Moorabool 500/220kV A2 Transformer
|  | Moorabool 500/220kV A2 Transformer | 1000 | 238 | 69.4 | 247.912 | 1500 | 387.6139 | 148.9201 | 415 | S | 24.79% | 27.67% | Moorabool 500/220kV A1 Transformer
* This is 5 minute short-term rating (N-1) available to the operator.
1 South Morang 330/220kV H2 Transformer is normally out of service under system normal conditions as it is used as a hot spare transformer.
Note on P118: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: CONTINGENCY SMTS_B3_H3_TTS_2 / fault on SMTS B3 will trip the no 2 bus which offloads the SMTS H3 Tx and SMTS - TTS no 2
Note on P120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: fault on SMTS B1 will trip the no 1 bus which offloads the SMTS H1 Tx and SMTS - TTS no 1 DISCONNECT BUS 373081

## Maximum demand 2
Table 2 — Maximum demand snapshot: Interconnector power flow and limits
Interconnector | Interconnector target (MW)1 | Import Limit (MW)2 | Export Limit (MW)3 | Import constraint equation | Import Constraint description | Export constraint equation | Export Constraint description
Vic–NSW | -64 | -64 | -64 | V>>NIL_MLGT_MLGT_R5 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | N>>BDBU_970_051 | Out = Bundey to Buronga (6F) 330kV line, avoid O/L Burrinjuck to Yass (970) on trip of Wagga to Lower Tumut (051) line, Feedback
Vic–SA (Heywood) | -30 | -30 | -30 | V>>NIL_MLGT_MLGT_R5 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | NRM_VIC1_SA1 | Negative Residue Management constraint for VIC to SA flow
Vic–SA (Murraylink) | 30 | 30 | 30 | V>>NIL_MLGT_MLGT_R5 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback | VSML_030 | Vic to SA on ML upper transfer limit of 30 MW
Tas–Vic (Basslink) | 456 | 393 | 456 | VTBL_ROC | Out=Nil, Rate of Change (Vic to Tas) constraint (200 MW / 5 Min) for Basslink | V>>NIL_MLGT_MLGT_R5 | Out = NIL, avoid O/L Moorabool to Geelong #1 or #2 on trip of other Moorabool to Geelong line, Yallourn W Unit 1 in 500 kV mode, Feedback
1 Note that actual interconnector power flows during a five-minute interval may deviate from their targets. Negative flows are in the import direction, whilst positive flows are in the export direction.
2 The import direction reflects southward flows on VNI and Basslink, and eastward flows on Heywood and Murraylink. Imports are reported as negative numbers, so that a positive import limit represents a forced export. This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 The export direction reflects northward flows on VNI and Basslink, and westward flows on Heywood and Murraylink. Exports are reported as positive numbers, so that a negative export limit represents a forced import.This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.

## High export to NSW 1
Table 3 — High export to NSW snapshot: DSN continuous and short-term ratings and loadings
Region | Voltage | Lines/transformers | Continuous rating (N) (MVA) | Continuous loading (N) (MW) | Continuous loading (N) (MVAr) | Continuous loading (N) (MVA) | Short–term rating* (N–1) (MVA) | Short-term loading (N-1) (MW) | Short-term loading (N-1) (MVAr) | Short-term loading (N-1) (MVA) | Rating type | (N) loading | (N–1) loading | Critical contingency
Northern Corridor | 330 kV | Dederang 330kV - Wodonga 330kV | 743 | 364.1505 | 94.7304 | 376.2704 | 743 | 478.3926 | 102.7179 | 489.2959 | D | 50.64% | 65.85% | Dederang 330kV - Murray 330kV 1
|  | Dederang 330kV - Murray 330kV 1 | 1185 | 417.082 | 0.88005 | 417.083 | 1303 | 706.6566 | 35.1948 | 707.5324 | D | 35.2% | 54.3% | Dederang 330kV - Murray 330kV 2
|  | Dederang 330kV - Murray 330kV 2 | 1185 | 413.3063 | 4.357 | 413.3293 | 1303 | 704.9175 | 29.8987 | 705.5513 | D | 34.88% | 54.15% | Dederang 330kV - Murray 330kV 1
|  | Dederang 330kV - South Morang 330kV 1 | 1145 | 493.8895 | 0.11094 | 493.8895 | 1343 | 834.236 | 148.2388 | 847.3042 | D | 43.13% | 63.09% | Dederang 330kV - South Morang 330kV 2
|  | Dederang 330kV - South Morang 330kV 2 | 1145 | 492.5602 | 0.11383 | 492.5602 | 1343 | 833.524 | 148.4273 | 846.6363 | D | 43.02% | 63.04% | Dederang 330kV - South Morang 330kV 1
| 220 kV | Dederang 220kV - Mount Beauty 220kV 1 | 369 | 131.3326 | 19.8159 | 132.8191 | 369 | 237.7605 | 30.5776 | 239.7187 | D | 35.99% | 64.96% | Dederang 220kV - Mount Beauty 220kV 2
|  | Dederang 220kV - Mount Beauty 220kV 2 | 369 | 131.3326 | 19.8159 | 132.8191 | 369 | 237.7605 | 30.5776 | 239.7187 | D | 35.99% | 64.96% | Dederang 220kV - Mount Beauty 220kV 1
|  | Dartmouth 220kV - Mount Beauty 220kV | 230 | 157.0296 | 10.4796 | 157.3789 | 230 | 157.0297 | 11.6983 | 157.4648 | D | 68.43% | 68.46% | -
|  | Bogong 220kV - Mount Beauty 220kV | 1064 | 3.8098e-06 | 0.91942 | 0.91942 | 1064 | 0.0001641 | 0.9317 | 0.9317 | D | 0.08641% | 0.08757% | -
|  | Mount Beauty 220kV - West Kiewa 220kV | 97 | 4.2178e-06 | 0.44064 | 0.44064 | 97 | 1.7669e-05 | 0.44028 | 0.44028 | S | 0.4543% | 0.4539% | -
|  | Eildon 220kV - Thomastown 220kV | 738 | 69.3692 | 92.4673 | 115.5954 | 738 | 158.4338 | 91.8161 | 183.116 | D | 15.66% | 24.81% | Dederang 330kV - South Morang 330kV 1
|  | Eildon 220kV - Mount Beauty 220kV 1 | 356 | 60.2976 | 34.8344 | 69.6364 | 356 | 104.1856 | 36.2683 | 110.3179 | D | 19.56% | 30.99% | Dederang 330kV - South Morang 330kV 1
|  | Eildon 220kV - Mount Beauty 220kV 2 | 356 | 60.2976 | 34.8344 | 69.6364 | 356 | 104.1856 | 36.2683 | 110.3179 | D | 19.56% | 30.99% | Dederang 330kV - South Morang 330kV 1
| 330/220 kV | Dederang 330/220kV H1 Transformer | 340 | 90.8842 | 13.2458 | 91.8444 | 400 | 136.2352 | 20.6116 | 137.7856 | S | 27.01% | 34.45% | Dederang 330kV - South Morang 330kV 1
|  | Dederang 330/220kV H2 Transformer | 340 | 81.6561 | 11.4864 | 82.4601 | 400 | 121.1877 | 17.8904 | 122.5011 | S | 24.25% | 30.63% | Dederang 330kV - South Morang 330kV 1
|  | Dederang 330/220kV H3 Transformer | 240 | 77.346 | 6.8768 | 77.6511 | 240 | 115.9773 | 10.9465 | 116.4927 | S | 32.35% | 48.54% | Dederang 330kV - South Morang 330kV 1
| 500/330 kV | South Morang 500/330kV F1 Transformer | 1000 | 528.3255 | 55.9632 | 531.2812 | 1200 | 874.8708 | 99.7012 | 880.5336 | S | 53.13% | 73.38% | South Morang 500/330 kV F2 Transformer
Greater Melbourne and Geelong |  | South Morang 500/330kV F2 Transformer | 1000 | 533.4492 | 59.5559 | 536.7634 | 1200 | 877.4288 | 102.1244 | 883.352 | S | 53.68% | 73.61% | South Morang 500/330 kV F1 Transformer
| 330/220 kV | South Morang 330/220kV H1 Transformer1 | 700 | 39.131 | 35.0034 | 52.5021 | 850 | 92.3276 | 18.9818 | 94.2587 | S | 7.5% | 11.09% | Ringwood 220kV- Rowville 220kV
|  | South Morang 330/220kV H2 Transformer | 700 | 0 | 0 | 0 | 850 | 0 | 0 | 0 | S | 0% | 0% | -
|  | South Morang 330/220kV H3 Transformer | 700 | 36.1485 | 2.9294 | 36.267 | 1000 | 78.5252 | 2.0269 | 78.5513 | S | 5.181% | 7.855% | Yallourn generating unit 4
* This is 5 minute short-term rating (N-1) available to the operator.
1 South Morang 330/220kV H2 Transformer is normally out of service under system normal conditions as it is used as a hot spare transformer.

## High export to NSW 2
Table 4 — High export to NSW snapshot: Interconnector power flow and limits
Interconnector | Interconnector target (MW)1 | Import Limit (MW)2 | Export Limit (MW)3 | Import constraint equation | Import Constraint description | Export constraint equation | Export Constraint description
Vic–NSW | 1476 | -627 | 1476 | N^^V_NIL_ARWBBA | Out = Nil, avoid voltage collapse in southern NSW for loss of Ballarat to Waubra to Ararat 220kV lines (this also trips Waubra, Ararat and Crowlands, Bulgana and Murra Warra WFs) | V>>N_NIL_65_66 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback
Vic–SA (Heywood) | -483 | -674 | -278 | SV_550_TEST | Out = Nil, SA to Vic on Heywood limit of 550 MW, limit for testing of Heywood interconnection upgrade | V::N_NIL_V1 | Out = NIL, prevent transient instability for fault and trip of a HWTS-SMTS 500 kV line, VIC accelerates. Yallourn W G1 on 220kV.
Vic–SA (Murraylink) | -54 | -125 | -54 | SVML_ROC_80 | Out=Nil, Rate of Change (SA to VIC) constraint (80 MW / 5 Min) for Murraylink | V>>N_NIL_65_66 | Out = Nil, avoid Murray to Upper Tumut(65) O/L on Murray to Lower Tumut(66) trip; Feedback
Tas–Vic (Basslink) | -459 | -459 | -265 | F_T++NIL_MG_R6 | Out = Nil, Raise 6 sec requirement for a Tasmania Synchronous Generation Event (both largest MW output and inertia), Basslink able to transfer FCAS | TVBL_ROC | Out=Nil, Rate of Change (Tas to Vic) constraint (200 MW / 5 Min) for Basslink
1 Note that actual interconnector power flows during a five-minute interval may deviate from their targets. Negative flows are in the import direction, whilst positive flows are in the export direction.
2 The import direction reflects southward flows on VNI and Basslink, and eastward flows on Heywood and Murraylink. Imports are reported as negative numbers, so that a positive import limit represents a forced export. This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.
3 The export direction reflects northward flows on VNI and Basslink, and westward flows on Heywood and Murraylink. Exports are reported as positive numbers, so that a negative export limit represents a forced import.This limit is based on the 5-min dispatch interval (MW) calculated by NEMDE. This limit considers network topology and dynamic equipment ratings. These limits are approximate and are derived from constraint equations that represent physical limitations only at the end of each interval.