| Victorian Transfer Limit Advice – System Normal 07/2026 A report for the National Electricity Market on transfer limits in the Victorian region |  |  |
| --- | --- | --- |

Important notice

Purpose

This publication has been prepared by VicGrid to provide information about the transfer limit equations for flows to, from and inside Victoria for voltage stability, transient stability, voltage oscillation and voltage unbalance limits or constraint equation performance and related issues, as at the date of publication.

Disclaimer

This document or the information in it may be subsequently updated or amended. This document does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. VicGrid has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.

Accordingly, to the maximum extent permitted by law, VicGrid and its officers, employees and consultants involved in the preparation of this document:

make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this document; and

are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.

Acknowledgement of Traditional Owners

We acknowledge and respect Victoria’s Traditional Owners as the original custodians of Victoria’s land and waters, their unique ability to care for Country and deep spiritual connection to it. We honour Elders past and present whose knowledge and wisdom has ensured the continuation of culture and traditional practices.

We are committed to genuinely partnering and meaningfully engaging with Victoria’s Traditional Owners and First Peoples to support the protection of Country, the maintenance of spiritual and cultural practices and their broader aspirations in the 21st century and beyond.

Acknowledgement

VicGrid acknowledges the cooperation and contribution of Victorian electricity industry participants in providing data and information used in this document.

Copyright

© 2026 VicGrid. The material in this publication may be used in accordance with the copyright permissions on VicGrid’s website.

Document Control

| Victorian Transfer Limit Advice – System Normal |  |  |
| --- | --- | --- |
| Version | Date | Changes |
| 36 | 20/07/2026 | Removed V^SML_BEKG and V^SML_X5_X3 from the system normal voltage stability limits. |
| 35 | 1/05/2026 | Added Bulgana BESS into V_NWVIC_GFT1_750, removed the Heywood import voltage collapse limit (V^^V_NIL_SWVIC). |
| 34 | 6/03/2026 | Updated to VicGrid template. Added maximum generator contingency section, added contingency size limit section, updated Victorian system strength minimum generator combinations, removed the HIC export voltage collapse limit (V^S_HYCP). |
| 33 | 25/09/2025 | Updated Vic system strength combinations based on review by AEMO Vic Planning. |
| 32 | 11/04/2025 | Updated Kerang limit and some limit equation terms. |
| 31 | 19/12/2024 | Added definitions of inverter/turbine off and blocking, added Victoria system strength combinations (from the SA and Vic TLA). |
| 30 | 30/10/2024 | Added modifications for Project Energy Connect – Stage 1. |
| 29 | 26/07/2024 | commissioning of Cressy Terminal Station (CRTS), adding Hawkesdale and Ryan Corner with the same factor as Macarthur WF and adding factors of several other plant into limit equations. |
| 28 | 8/03/2024 | Added Hazelwood battery and Broken Hill battery outputs to all relevant limits, added Wagga 330kV 100 MVAr capacitor bank term to the 2xAPD limit, added Wyalong and West Wyalong solar farm terms to the 2XAPD limit. |
| 27 | 2/11/2023 | Updated Kerang voltage collapse limit w.r.t changes to VFRB scheme and added the South West Victoria Voltage Oscillation Limit. |
| 26 | 29/08/2022 | Added South West Victoria Voltage Stability Limit. |
| 25 | 16/08/2022 | Updated Victorian export voltage stability limit for loss of both APD potlines. |
| 24 | 1/08/2022 | Minor tweaks to the new AEMO template. |
| 23 | 31/03/2022 | Updated to latest AEMO template, added section on update process for limits, Updated VIC-NSW transient stability limit equations. |
| 22 | 11/11/2021 | Updated Kerang voltage collapse limit- Bendigo 66 kV capacitors term added. |
| 21 | 16/08/2021 | Updated Kerang voltage collapse limit. |
| 20 | 17/03/2021 | Added new Kerang voltage collapse Hard limit. |
| 19 | 10/02/2021 | Updated Victorian export voltage stability limit for loss of both APD potlines, minor editing corrections. |
| 18 | 1/12/2020 | Update to definition of SW_NSW_GEN for VIC import voltage limits for Loss of Largest Vic Generator (Latrobe Valley studies) and loss of the Ballarat – Waubra-Ararat 220kV line and up to 800 MW of generation (North West Victoria). |
| 17 | 8/10/2020 | Updated Victorian export voltage stability limit for loss of both APD potlines, minor editing corrections and updates to URLs. |
| 16 | 25/05/2020 | Updated section 3.2 with new Victorian voltage stability import limit. |
| 15 | 1/05/2020 | Removed the output and inverter limits of Broken Hill SF, Bannerton SF, Gannawarra SF, Karadoc SF and Wemen SF. |
| 14 | 24/01/2020 | Updated Victorian voltage stability import limit. |
| 13 | 8/01/2020 | Added north-west Victoria voltage collapse limit. |
| 12 | 8/11/2019 | Updated Victorian export voltage stability limit on Murraylink for the loss of either the Darlington Point to Balranald or Balranald to Buronga 220 kV lines. Added 100 MW offset to NSW to Victoria voltage stability limit. |
| 11 | 19/09/2019 | Added Victorian export voltage stability limit on Murraylink for the loss of the Bendigo to Kerang 220 kV line. Updated Definitions to include new generators. Added voltage oscillation limits for solar farms for north-west Vic and south-west NSW. |
| 10 | 15/03/2019 | Updated Voltage Stability Import limit, NILV and NILS Transient Stability Export limits. |
| 9 | 23/11/2018 | Updated Voltage Stability Import limit & applied new template. |
| 8 | 23/07/2018 | Updated Voltage Stability Import limit with additional terms to reflect impact of Victorian hydro (Kiewa scheme), Guthega, Jindabyne and additional reactive plant in southern NSW. |
| 7 | 14/12/2017 | Updated Voltage Stability Import limit, removed reference to Hazelwood Power Station and Victorian synchronous condenser terms. Updated disclaimer. |
| 6 | 31/01/2017 | Updated disclaimer and added offset for decommissioned synchronous condensers in Victoria in the voltage collapse limit. |
| 5 | 22/12/2016 | Updated for Heywood Upgrade post series caps (system normal). Edits to document text. Added Heywood voltage collapse limit. |
| 4 | 10/04/2016 | Converted to new AEMO template. Updated for third transformer at Heywood (system normal). Edits to document text. |
| 3 | 16/05/2014 | Added Victorian import limit equation and updated to new AEMO template. |
| 2 | 14/11/2013 | Fixed table formatting issues, corrected definitions, Updated Equation, with term for Mount Mercer Wind Farm (MMWF) megawatt (MW) output. |
| 1 | 23/12/2012 | Initial version. |

Contents

1	Introduction	1

1.1	Other VicGrid publications	1

1.2	Calculating transient and voltage stability limits	1

1.3	Inverter and Turbine limits	2

1.4	Conversion to constraint equations	2

1.5	Maximum generator contingency size	2

2	System Normal Transient Stability Limits	3

2.1	NIL_V	4

2.2	NIL_O	5

3	System Normal Voltage Stability Limits	6

3.1	NIL_VI_BLVG	7

3.2	NIL_VI_ARWBBA	8

3.3	V^N_2xAPD	9

3.4	NIL_KERANG	10

4	System Normal Voltage Oscillation Limits	12

4.1	V_SH_DD_MAC_FLT_965	12

5	Contingency Size Limit	13

5.1	V_NWVIC_GFT1_750	13

6	Victorian System Strength Requirements	14

A1	Measures and Definitions	16

A1.1	Units of Measure	16

A1.2	Parameter Definitions	16

A2	Glossary	23

List of Tables

Table 1: Limit Equation major updates	2

Table 2: System normal transient stability limits	3

Table 3: NIL_V export limit equation coefficients	4

Table 4: NIL_O export limit equation coefficients	5

Table 5: System normal voltage stability limits	6

Table 6: NIL_VI_BLVG coefficients	7

Table 7: NIL_VI_ARWBBA coefficients	8

Table 8: V^N_2xAPD coefficients	9

Table 9: NIL_KERANG Disabled	11

Table 10: NIL_KERANG Enabled	11

Table 11: Victorian system strength minimum generator combinations for a secure state	14

# Introduction

VicGrid is responsible for calculating the maximum transient and voltage stability limits into and out of Victoria (National Electricity Rules (NER) S5.1.2.3) in accordance with Power System Stability Guidelines. This document describes the values for these transfer limits for system normal conditions (that is, when all transmission elements are in service) in Victoria.

This limits advice document also describes the methodology used by VicGrid to determine the transient and voltage stability limits.

The limit equations for cases where one or more transmission elements are out of service are described in separate documents:

Victorian Transient Limit Advice – Outages.

Victorian Transfer Limit Advice – Multiple Outages.

Victorian Transfer Limit Advice – Outages in Adjacent Regions.

## Other VicGrid publications

Other limit advice documents are located at https://www.vicgrid.com.au/transmission-planning/planning-the-energy-grid.

## Calculating transient and voltage stability limits

Transfer limit equations are developed for power transfers into and out of Victoria (known as import and export limits respectively). Maximum export is limited by transient stability, whereas maximum import is determined by voltage stability.

Transient stability limit equations are derived from a large number of transient stability studies. Stability studies are based on the application of a 2-phase to ground fault at the most critical fault location.

Voltage stability limit equations are derived from a large number of load flow studies. Studies consider the trip of a large generator, the loss of Basslink when exporting from Tasmania (Tas) to Victoria (Vic), and where appropriate the fault and trip of a critical transmission line or transformer.

### Methodology

The methodology for calculating voltage and transient stability limits is:

Generate a set of Power System Simulator for Engineering (PSS/E) cases to represent a wide range of operating conditions.

Execute a binary search algorithm to search for limiting interconnector power transfer.

Linear regression and statistical limit determination.

### Updates

Updates to the Victorian transfer limits are triggered due to:

generation or transmission or control scheme changes

issues are raised from online monitoring tool results or from regular stability limit benchmarking that AEMO performs

revised generator models

Generally major “clean sheet” reviews to the Victorian limit equations occur every 4-5 years – these are detailed in section 1.2.3. Normally generator or network changes can be updated by performing smaller studies and reviewing and updating the regression analysis.

### Limit equation major updates

Table 1: Limit Equation major updates

| Equation | Section | Last Major update |
| --- | --- | --- |
| Vic to NSW – loss of Hazelwood – South Morang line | 2 | March 2022 |
| Vic to NSW – loss of APD | 3.3 | May 2019 |
| NSW to Vic– loss of largest gen / Basslink | 3.1 | March 2020 |
| NSW to Vic – loss of largest gen in NW Vic | 3.2 | May 2020 |
| Kerang voltage collapse | 3.4 | August 2021 |

## Inverter and Turbine limits

The following terminology is used by VicGrid/AEMO for limitations on plant with turbines and inverters.

Disconnected – The inverters or turbines are physically disconnected from the power system through the opening of a circuit breaker or through the participant advising VicGrid/AEMO that the inverters are physically disconnected from the power system via some other means.

Blocked – The inverters or turbines enter a state where they will not respond to any power system changes and are essentially no longer operating/online. For the avoidance of doubt when an inverter or turbine is blocked it will provide no MWs or MVARs and will be prevented from firing and therefore does not impact system strength. When “Blocked” the inverter or turbine may remain physically connected to the power system. In the past AEMO has referred to this in the limits advice as “Pause Mode”

Constrained to Zero – The inverter or turbines are constrained to 0 MW output via the local plant controller, or constraints and NEMDE.

## Conversion to constraint equations

This document does not describe how AEMO implements these limit equations as constraint equations in the National Electricity Market (NEM) market systems. That is covered in the Constraint Formulation Guidelines, Constraint Naming Guidelines and Constraint Implementation Guidelines. These documents are located in the Congestion Information Resource on the AEMO website, at: https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/system-operations/congestion-information-resource.

## Maximum generator contingency size

VicGrid assume a maximum allowable generator contingency size of 750 MW when developing all limits. This requirement aims to ensure that no single credible contingency results in a loss of generation exceeding 750 MW, even during a prior network outage scenario.

The 750 MW value is consistent with an acceptable contingency size identified in the 2025 VAPR and is comparable with current Frequency Control Ancillary Service (FCAS) acquisition requirements. Applying a consistent 750 MW contingency limit across the network ensures system security and keeps contingency events within established NEM operational parameters.

# System Normal Transient Stability Limits

There are two system normal Vic-NSW export transient stability limit equations to prevent angle separation of Victoria (Vic), Queensland (Qld), and South Australian (SA) generators for a fault on one Hazelwood to South Morang 500 kilovolt (kV) line. These are referred to as NIL_V, and NIL_O. decelerating equations.

NIL_V manages conditions when rotor angles of Victoria synchronous machines accelerate ahead of rotor angles of synchronous machines of all the other states. The NIL_O manages conditions when rotor angles of the synchronous machines in states other than Victoria accelerating or decelerating against the rotor angles of synchronous machines in all the other states.

Table 2: System normal transient stability limits

| Equation | Description of Limit |
| --- | --- |
| NIL_V | Victorian transient stability export limit on the Vic to NSW interconnectors for the two phase to ground fault and trip of Hazelwood – South Morang 500 kV line where instability occurs due to rotor angles of Vic synchronous machines accelerating away from the rotor angles of synchronous machines of all the other regions. |
| NIL_O | Victorian transient stability export limit on the Vic to NSW interconnectors for the two phase to ground fault and trip of Hazelwood – South Morang 500 kV line where instability occurs due to rotor angles of synchronous machines in regions other than Victoria accelerating or decelerating away from the rotor angles of synchronous machines in all the other states. |

The transfer limit between Vic and NSW is the minimum megawatt (MW) transfer of all enabled limits at a given point in time and depends on system conditions and plant parameters.

Each limit equation is of the form:

Victoria to NSW ≤ Sum [Term Values * Coefficients]

## NIL_V

Table 3: NIL_V export limit equation coefficients

| Term | Coefficient |
| --- | --- |
| Basslink | 0.3978 |
| Vic to SA (Heywood) | -0.4780 |
| Vic to SA (Heywood)^2 | -0.0002605 |
| Vic to SA (Murraylink) | -0.4918 |
| LV 220 Gen | 0.3604 |
| Murray Gen | 0.7863 |
| Kiewa Gen | 0.8963 |
| Vic Demand - State Grid Load - APD Load | -0.3394 |
| APD Load | -0.6054 |
| State Grid Load North | -0.3671 |
| State Grid Load South | -0.8245 |
| Vic Wind & Solar | 0.4320 |
| STH_NSW_WIND_SOLAR_GEN | -0.1173 |
| EPS Inertia | 15.47 |
| MOPS Inertia | 7.085 |
| Vic Metro Gen Inertia | 6.995 |
| SNOWY Inertia | 3.253 |
| LV 500 Inertia | 7.953 |
| LOY_YANG_PS_UNITS | 39.73 |
| Intercept | 970.6 |
| Confidence Level (95%) offset | -129 |

## NIL_O

Table 4: NIL_O export limit equation coefficients

| Term | Coefficient |
| --- | --- |
| Basslink | 0.3192 |
| Vic to SA (Heywood) | -0.3544 |
| Vic to SA (Murraylink) | -0.5389 |
| LV 220 Gen | 0.3111 |
| Kiewa Gen | 0.9475 |
| Murray Gen | 0.7631 |
| Vic Demand - State Grid Load - APD Load | -0.2514 |
| State Grid Load North | -0.4889 |
| State Grid Load South | -0.6331 |
| Vic Wind & Solar | 0.3577 |
| STH_NSW_WIND_SOLAR_GEN | -0.2363 |
| EPS Inertia | 8.3487 |
| Vic Metro Gen Inertia | 6.6200 |
| LV 500 Inertia | 7.3391 |
| MOPS Inertia | 4.4303 |
| SNOWY Inertia | 3.2105 |
| APD Load | -0.2801 |
| LTUM3SC | 22.80 |
| Intercept | 929.7 |
| Confidence Level (95%) offset | -158.7 |

# System Normal Voltage Stability Limits

S5.1.8 in the NER specifies the requirements for voltage stability as:

N-1 QV curve knee point must be greater than 1% of the bus three phase fault level in MVA.

The bus voltage after the contingency must be between 0.90 – 1.10 p.u.

Table 5: System normal voltage stability limits

| Equation | Description of Limit |
| --- | --- |
| NIL_VI_BLVG | Vic voltage stability import limit from NSW to Vic for trip of Basslink or the largest Vic generator. |
| NIL_VI_ARWBBA | Vic voltage stability import limit from NSW to Vic for trip of the Ararat to Waubra to Ballarat 220 kV line |
| V^N_2xAPD | Vic voltage stability export limit from Vic to NSW for fault and trip of both APD potlines. |
| NIL_KERANG | Vic voltage stability limit from Wemen to Kerang 220 kV line flow for the trip of Crowlands to Bulgana to Horsham or Horsham to Murra Warra to Kiamal 220kV line. |

## NIL_VI_BLVG

For NSW to Vic transfers, a single limit equation is required under system normal conditions to prevent voltage collapse in southern NSW and northern Vic following the loss of Basslink or the loss of the largest Vic generator.

Voltage collapse under import conditions is observed to predominately occur in Southern NSW.

The limit equation for NSW to Vic is of the form:

NSW to Victoria ≤ -1 * Sum [Term Values * Coefficients]

Table 6: NIL_VI_BLVG coefficients

| Term | Coefficient |
| --- | --- |
| Intercept | -1313 |
| Vic to SA (Murraylink) | -0.1187 |
| Contingent MW | 0.4875 |
| STH_NSW | 0.4709 |
| SE_NSW_WND_SOL_GEN | -0.1179 |
| SW_NSW_GEN – UQT_GEN | -0.3798 |
| UTUM1SC+UTUM2SC | -13.6 |
| LTUM3SC | -67.5 |
| MSS2SC | -50.1 |
| WOTSCap | -0.3496 |
| DD220Cap | -0.3179 |
| DD330Cap | -0.2133 |
| WAGGACap | -0.1299 |
| CANCap | -0.2367 |
| YASSCap | -0.291 |
| DLPT220 | -0.1097 |
| MSSReac | -0.2668 |
| YASSReac | -0.1927 |
| BANReac | -0.08229 |
| U_TUMUT_Gen | -0.5976 |
| L_TUMUT_Gen | -0.3895 |
| Murray Gen | 0.4834 |
| UQT Gen | -0.491 |
| BKNH GEN + SILVERTON WF MW | -.7145 |
| Num. MSS1 on | -23.99 |
| GEN BOPS on | -31.77 |
| GEN WKPS on | -5.022 |
| BOPS+MKPS GEN | 0.2452 |
| Confidence Level (95%) offset | 89 |

## NIL_VI_ARWBBA

On a trip of the Ballarat to Waubra to Ararat 220 kV line the Ararat, Bulgana, Crowlands, Murra Warra and Waubra wind farms are also tripped. A single limit equation is required under system normal conditions to prevent voltage collapse in southern NSW following the loss of Ballarat to Waubra to Ararat 220 kV line and subsequentially trip of the above wind farms.

The limit equation for NSW to Vic is of the form:

NSW to Victoria ≤ Sum [Term Values * Coefficients]

Table 7: NIL_VI_ARWBBA coefficients

| Term | Coefficient |
| --- | --- |
| STH_NSW | -0.468 |
| SW_NSW_GEN | 0.5024 |
| SE_NSW_WND_SOL_GEN | 0.0901 |
| L_TUMUT_Gen | 0.3918 |
| Murray Gen | -0.3065 |
| U_TUMUT_Gen | 0.4359 |
| BRKNHLSF_SilvWF | 1.0075 |
| ROTS_SVC_MVAR | 0.7543 |
| MSSReac | 0.3315 |
| Q2-BURNGA 220 | 1.1904 |
| DLPT220 | 4.4586 |
| Q2-DENILQ_132 | 7.0319 |
| YASSCap | 0.3292 |
| YASSReac | 0.9406 |
| LTUM3SC | 51.5951 |
| MSS2SC | 43.2052 |
| NW_VIC_WF_cont | -0.867 |
| Intercept | 1910 |
| Confidence Level (95%) offset | -170 |

## V^N_2xAPD

For VIC to NSW transfers, a single limit equation is required under system normal conditions to prevent voltage collapse in the Murray region following the loss of both APD potlines.

The limit equation for VIC to NSW is of the form:

Victoria to NSW ≤ Sum [Term Values * Coefficients]

Table 8: V^N_2xAPD coefficients

| Term | Coefficient |
| --- | --- |
| Intercept | 1500 |
| Vic to SA (Murraylink) | -0.1921 |
| VIC_G1__MW | 0.4731 |
| JBE Pump | 0.8977 |
| MSS2SC | 63 |
| MSSReac | 0.3771 |
| NSW_G1_ MW | -0.0510 |
| LTUM PUMP MW | -0.2267 |
| LTUM3SC | 35 |
| NSW_ASG1 | -0.0620 |
| Q_SS_YASS | 0.1268 |
| NSW_G2 | -0.4719 |
| NSW_ASG2 | -0.5502 |
| QC_SH2 | 0.3718 |
| NSW_ASG3 | -0.5631 |
| VIC_ASGZ2 | 0.1873 |
| Confidence Level (95%) offset | -110 |

## NIL_KERANG

To prevent voltage collapse at Kerang, Koorangie or Wemen a limit equation is required under system normal conditions following the loss of the Crowlands to Bulgana to Horsham or Horsham to Murra Warra to Kiamal 220kV line.

The limit equation is of the form:

Flow from Wemen to Koorangie ≤ Sum [Term Values * Coefficients]

### Murraylink VFRB disabled

Table 9: NIL_KERANG Disabled

| Term | Coefficient |
| --- | --- |
| Intercept | 280 |
| KGTS SVC Status | 17.66 |
| RCTS-MLK_MVAR | -0.1769 |
| Vic to SA (Murraylink) | -0.0773 |
| Q3-KERANG 66 | 0.26 |
| WETS Load | -1.733 |
| BETS Load | 0.2190 |
| Q3-BENDIGO 66 | 0.1 |
| Koorangie BESS MW | -0.3476 |
| Confidence Level (95%) offset | -41.33 |

### Murraylink VFRB enabled

Table 10: NIL_KERANG Enabled

| Term | Offset |
| --- | --- |
| Offset to system normal NIL_KERANG Disabled | -45 |

# System Normal Voltage Oscillation Limits

Voltage oscillations and associated instability can occur in parts of the power system that have low system strength. To mitigate such oscillations in the power system, voltage oscillatory stability limits are determined for low system strength conditions.

Simulations of large disturbances such as two-phase to ground fault and trip of critical lines are undertaken using PSCAD to determine if the voltage oscillations occur in the power system post-contingency. Large disturbance simulations of several operating conditions are undertaken to determine the limiting operating conditions of the power system which prevent voltage oscillations from occurring.

## V_SH_DD_MAC_FLT_965

To prevent voltage oscillations for the contingencies in South West Victoria the following limit is applied:

If (Heywood interconnector power flow (in SA-Vic direction) > = 500 MW):

(Stockyard Hill wind farm MW + Dundonnell wind farm MW + Macarthur wind farm MW + Hawkesdale wind farm MW + Ryan Corner wind farm MW) < = 965 MW

# Contingency Size Limit

## V_NWVIC_GFT1_750

The 220 kV Generator Fast Trip scheme (GFT1), inherent tripping of Waubra WF and runback of Bulgana BESS in North-West Victoria together currently have the potential to create a contingency size of greater than 750MW and up to a maximum of 1177MW following the contingency of the ARTS-WBTS-BATS 220kV Line. The actual contingency size will depend on the real time output levels of the generators involved in the scheme.

The generators currently included in GFT1 are listed below with their associated maximum output capacity:

- Ararat WF (241 MW)

- Crowlands WF (79 MW)

- Bulgana WF (204 MW)

- Murra Warra WF (441 MW)

The Waubra windfarm maximum output capacity is:

- Waubra WF (192 MW)

The Bulgana BESS maximum output capacity is:

- Bulgana BESS (20 MW)

The limit is formulated as follows:

All WFs associated with GFT1 MW + Inherent tripping of Waubra WF MW + Runback of Bulgana BESS MW ≤ 750 MW

It should be noted that Waubra WF is a non-scheduled generator, and as such the total constraint on the windfarms which are part of GFT 1 and Bulgana BESS is:

≤ 750 MW – Waubra WF generation output

# Victorian System Strength Requirements

Table 11 summarises the combinations of synchronous generating units that would provide sufficient system strength in Victoria to withstand a credible fault and loss of a synchronous unit (the most critical contingency for these combinations is loss of a Loy Yang A unit). This limit applies during system normal and outage conditions.

Table 11: Victorian system strength minimum generator combinations for a secure state

2 Loy Yang Units

| Combination | Loy Yang (A or B) | Yallourn | Ararat Syncon | Newport | Dartmouth | Bogong* | Murray2# | Mortlake | Jeeralang (A or B) | Valley Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VIC_2A | 2 | 3 | 1 | 1 |  |  | 1 |  | 1 |  |  |
| VIC_2B | 2 | 3 | 1 | 1 |  |  | 1 |  |  | 1 |  |
| VIC_2C | 2 | 3 | 1 |  | 1 |  |  |  | 3 |  |  |
| VIC_2D | 2 | 3 | 1 |  | 1 |  |  |  | 1 | 2 |  |
| VIC_2E | 2 | 3 | 1 |  | 1 |  |  |  | 2 | 1 |  |

3 Loy Yang Units

| Combination | Loy Yang (A or B) | Yallourn | Ararat Syncon | Newport | Dartmouth | Bogong* | Murray2# | Mortlake | Jeeralang (A or B) | Valley Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VIC_3A | 3 | 3 |  |  |  |  |  |  |  |  |  |
| VIC_3B | 3 | 2 | 1 |  |  |  |  |  |  |  |  |
| VIC_3C | 3 | 1 | 1 |  |  |  |  |  |  | 3 |  |
| VIC_3D | 3 | 1 |  |  |  |  |  |  | 3 |  |  |
| VIC_3E | 3 | 1 |  |  |  |  |  |  | 1 | 2 |  |
| VIC_3F | 3 | 1 |  |  |  |  |  |  | 2 | 1 |  |
| VIC_3G | 3 | 1 |  | 1 |  |  |  |  |  |  |  |
| VIC_3H | 3 |  |  | 1 |  |  |  |  | 3 |  |  |
| VIC_3I | 3 |  | 1 | 1 |  |  | 2 |  | 1 |  |  |
| VIC_3J | 3 |  | 1 | 1 |  |  | 2 |  |  | 1 |  |
| VIC_3K | 3 |  | 1 | 1 | 1 | 1 |  |  | 1 |  |  |
| VIC_3L | 3 |  | 1 | 1 | 1 | 1 |  |  |  | 1 |  |
| VIC_3M | 3 |  | 1 | 1 |  |  |  |  |  | 3 |  |
| VIC_3N | 3 |  | 1 | 1 |  |  |  |  | 1 | 2 |  |
| VIC_3O | 3 |  | 1 | 1 |  |  |  |  | 2 | 1 |  |
| VIC_3P | 3 |  | 1 |  |  |  | 2 |  | 5 |  |  |
| VIC_3Q | 3 |  | 1 |  |  |  | 2 |  | 3 | 1 |  |
| VIC_3R | 3 |  | 1 |  |  |  | 2 |  | 2 | 2 |  |
| VIC_3S | 3 |  | 1 |  |  |  | 2 |  | 1 | 4 |  |
| VIC_3T | 3 |  | 1 |  |  |  | 2 |  |  | 6 |  |
| VIC_3U | 3 |  | 1 |  | 1 | 1 | 2 |  | 3 |  |  |
| VIC_3V | 3 |  | 1 |  | 1 | 1 | 2 |  | 2 | 1 |  |
| VIC_3W | 3 |  | 1 |  | 1 | 1 | 2 |  | 1 | 2 |  |
| VIC_3X | 3 |  | 1 |  | 1 | 1 | 2 |  |  | 4 |  |

4 Loy Yang Units

| Combination | Loy Yang (A or B) | Yallourn | Ararat Syncon | Newport | Dartmouth | Bogong* | Murray2# | Mortlake | Jeeralang (A or B) | Valley Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VIC_4A | 4 | 1 |  |  |  |  |  |  |  |  |  |
| VIC_4B | 4 |  |  | 1 |  |  |  |  |  |  |  |
| VIC_4C | 4 |  |  |  | 1 | 1 |  |  |  |  |  |
| VIC_4D | 4 |  |  |  | 1 |  | 1 |  |  |  |  |
| VIC_4E | 4 |  |  |  |  |  | 2 |  |  |  |  |
| VIC_4F | 4 |  |  |  |  |  |  | 1 |  |  |  |
| VIC_4G | 4 |  |  |  |  |  |  |  | 1 | 1 |  |
| VIC_4H | 4 |  |  |  |  |  |  |  | 2 |  |  |
| VIC_4I | 4 |  |  |  |  |  |  |  |  | 2 |  |

5 or more Loy Yang Units

| Combination | Loy Yang (A or B) | Yallourn | Ararat Syncon | Newport | Dartmouth | Bogong* | Murray2# | Mortlake | Jeeralang (A or B) | Valley Power |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| VIC_5A | 5 |  |  |  |  |  | 1 |  |  |  |  |
| VIC_5B | 5 |  |  |  |  |  |  |  | 1 |  |  |
| VIC_5C | 5 |  |  |  |  |  |  |  |  | 1 |  |
| VIC_6A | 6 |  |  |  |  |  |  |  |  |  |  |

* McKay Creek units are not equivalent to a Bogong unit.

# Murray 2 refers to Murray units 11 to 14. The units operating in generator or synchronous condenser mode will satisfy this requirement.

Measures and Definitions

Units of Measure

| kV | Kilovolt |
| --- | --- |
| MVA | Megavolt amperes |
| MVAR | Megavolt amperes reactive |
| MW | A Megawatt (MW) is one million watts. A watt (W) is a measure of power and is defined as one joule per second and it measures the rate of energy conversion or transfer. |
| MW.sec | Megawatt seconds – a measure of the inertia of a generating unit. |
| kV | kilovolt |

Parameter Definitions

| Abbreviation | Definition |
| --- | --- |
| 220 kV Caps | MVAR output from capacitors connected at 220 kV busbars (i.e. Altona, Brooklyn, Dederang, Fishermans Bend, Keilor, Moorabool, Rowville, Ringwood, Templestowe and Thomastown) |
| 330 kV Caps | MVAR output from capacitors connected at 330 kV busbars (i.e. Dederang and Wodonga). |
| APD–HYTS_MVAR | Alcoa Portland smelter (APD) reactive power export (measured at 500 kV feeders). A negative value indicates that APD is importing MVAr. |
| APD–HYTS_MW | APD real power export (measured at 500 kV feeders. A negative value indicates that APD is importing MW). |
| APD Load | APD MW load at 33 kV and 22 kV |
| BANReac | MVAR output of Bannaby reactors. Values associated with this term are negative. |
| Basslink | MW flow on the Basslink interconnector (measured at the receiving end) |
| BETS Load | BETS Load Bendigo (BETS) customer load (MW) |
| Both TAIL-SESS Series Caps Out | Both Tailem Bend – South East series caps out of service (1= Both series caps are out of service) |
| BKNH GEN | MW output from Broken Hill Generation and Broken Hill battery (discharging is positive and charging is negative) |
| BOPS+MKPS GEN | MW output from Bogong and McKay Power Station [BOPS & MKPS]. |
| BRKNHLSF_SilvWF | MW output from Broken Hill SF, Silverton WF and Broken Hill battery (discharging is positive and charging is negative) |
| CANCap | MVAR output of Canberra 220 kV capacitor banks. Values associated with this term are positive. |
| CMACap | MVAR output of Cooma capacitor banks. Values associated with this term are positive. |
| Contingent MW | Maximum of: MW Transfer from Tas to Vic via Basslink (measured at Loy Yang). Values associated with this term are positive for flows from Tas to Vic. MW output of a single generating unit in Vic (MW associated with the contingency: Loss of the Largest Generator). Values associated with this term are positive. |
| CUECap | MVAR output of Queanbeyan capacitor banks. Values associated with this term are positive. |
| DD220Cap | MVAR output of Dederang 220 kV capacitor banks. Values associated with this term are positive. |
| DD330Cap | MVAR output of Dederang 330 kV capacitor banks. Values associated with this term are positive. |
| DLPT220 | MVAR output of Darlington Point 220 kV reactors. Values associated with this term are negative. |
| DLPTshunt | MVAR output of Darlington Point shunt devices. Values associated with this term can be positive or negative |
| DPS GEN | MW output from Dartmouth Power Station [DPS]. |
| EPS Inertia | Inertia from Eildon Power Station (EPS). Inertia is on a 100 MVA base (MW.sec / 100 MVA) as per EMS. |
| GEN EPS on | Number of Eildon Power station (EPS) units online. |
| GEN DPS on | Number of Dartmouth Power station units online [DPS]. |
| GEN BOPS on | Number of Bogong Power station units online [BOPS]. |
| GEN MKPS on | Number of McKay Power station units online [MKPS]. |
| GEN WKPS on | Number of West Kiewa Power station units online [WKPS]. |
| Guthega GEN | MW output from Guthega Power Station [GGA]. |
| Guthega Inertia | Inertia from Guthega Power Station [GGA]. Inertia is on a 100 MVA base (MW.sec / 100 MVA) as per EMS. |
| HOTS+KGTS_SVC_MVAR | MVAR contribution from Horsham and Kerang SVCs. |
| HOTS_TX1_TX2 MW | Sum of MW flow on Horsham B2 and B3 220/66 kV transformers. Positive value indicates power flow from HV to LV side. |
| HOTS_TX1_TX2 MVAR | Sum of MVAR flow on Horsham B2 and B3 220/66 kV transformers. Positive value indicates power flow from HV to LV side. |
| HUME GEN | MW output from Hume Power station (Victorian and NSW connection) |
| HUME NSW GEN | MW output from Hume Power station (NSW connection) |
| HYTS_CAP_Status | Heywood capacitor status (1 = capacitor in service). |
| JBE Pump | MW at Jindabyne Power Station [JBE]. Values associated with this term are negative. |
| KGTSreac | MVAR contribution from Kerang terminal station 66 kV reactors. Values associated with this term are negative. |
| KGTS Load | MW load at Kerang terminal station. |
| KGTS SVC Status | Kerang SVC status. This term is equal to 1 when the SVC is in service, and equal to 0 when the SVC is out of service. |
| Kiewa Gen | MW output from Kiewa hydro scheme generators (Bogong, Clover, Dartmouth, Mckay and West Kiewa). |
| Kiewa Inertia | Inertia from Kiewa hydro scheme generators (Bogong, Clover, Dartmouth, McKay and West Kiewa). Inertia is on a 100 MVA base (MW.sec / 100 MVA). |
| Koorangie BESS MW | Koorangie BESS MW output (charging is negative and discharging is positive). |
| LOY_YANG_PS_UNITS | Number of generators in service in Loy Yang A and B power stations. |
| LTUM GEN MW | MW output from Lower Tumut 3 power station when generating (LTSS). Values associated with this term are positive. |
| L_TUMUT_Gen | MW output from Lower Tumut 3 power station (LTSS). Values associated with this term can be positive or negative due to the ability of Lower Tumut units to operate in pumping mode |
| LTUM PUMP MW | MW output from at Lower Tumut 3 when in pump mode [LTUM]. Values associated with this term are negative. |
| LTUM3SC | Number of generator units operating as synchronous condensers at Lower Tumut. |
| LV 220 Gen | MW output from Latrobe Valley generation on the 220 kV network (Yallourn W2, 3, and 4, and Yallourn unit 1 when connected to the 220 kV network). |
| LV 220 Inertia | Inertia associated with Latrobe Valley generation on the 220 kV network (Yallourn W2, 3, and 4, and Yallourn unit 1 when connected to the 220 kV network). |
| LV 500 Inertia | Inertia associated with Latrobe Valley generation on the 500 kV network (Loy Yang (A, B, and Valley Power), Jeeralang, Bairnsdale, and Yallourn W unit 1 when connected to the 500 kV network). |
| MBTS Gen | Generation connected at Mount Beauty. This includes Clover, Dartmouth, MacKay Creek, Bogong and West Kiewa. |
| MOPS Inertia | Inertia from Mortlake Power Station (MOPS). Inertia is on a 100 MVA base (MW.sec / 100 MVA) as per EMS. |
| MSS2SC | Number of generator units operating as synchronous condensers at Murray 2. |
| MSSReac | MVAR output of Murray reactors. Values associated with this term are negative. |
| Murray Gen | MW output from Murray Power Station (Murray 1 and Murray 2). |
| Num. LTUM3 on | Number of generator units operating at Lower Tumut. |
| Num. MSS1 on | Number of generator units operating at Murray 1. |
| Num. MSS2 on | Number of generator units operating at Murray 2. |
| Num. ROTS SVC | Number of Static Var Compensators (SVCs) at Rowville in service. |
| Num. SESS SVC | Number of SVCs at South East in service. |
| Num. UTUM1+2 on | Number of generator units operating at upper Tumut 1 and 2. |
| NSWd- SW_NSW | NSW demand (customer load + losses) minus the load in southern NSW. |
| NSW_ASG1 | MW output (Positive) from the following farms: BANGO__WF, BOCO_R__WF, CAPITL__WF, COLLEC_WF, CROOKW__WF, CULERN__WF, GUNNING_WF, GULLEN__WF, GULLEN__SF, BIALA__WF, TARALG___WF, WOODLN__WF, Walla Walla SF |
| NSW_ASG2 | MW output (Positive) from the following farms: BOMEN__SF, COLEMB__SF, COROWS_GEN, DARLIN__SF, FINLYS__SF, GRIFTH__SF, HILLST__SF, JEMALO__SF, JUNEE__SF, SEBAST_GEN, WAGGAN__SF, Wyalong SF, West Wyalong SF |
| NSW_ASG3 | MW output (Positive) from the following farms BRKNHL__SF, LIMON __SF, SILVER___WF, SUNRAY__SF and Broken Hill battery output (discharging is positive and charging is negative) |
| NSW CAN LOAD pos | Load in Canberra is the sum of customer load at the following (Zone 7) bulk supply points: Lower Tumut (LTPG1-6, LTP-330), Upper Tumut (UTP_G1-8), East Lake (EST-132), Belconnen (BLC-132), Causeway (CAU-132), Cooma (CMA-66, CMA-132), City East (CITI-132), Civic (CIV-132), Gilmore (GIL-132), Gold Creek (GCR-132), Latham (LAT-132), Geehi Dam (GEE-132), Queanbeyan (QUE-66, QUE-132), Theodore (THE-132), Wanniassa (WAI-132), Woden (WOD-132), Munyang (MNY-66). |
| NSW_G1_ MW | MW output (Positive) from the following generators. Note that unit should be operating as a generator. BLOWRG, BURNJK , JOUNAM, KANGVL, BENDLA, LWTUMT, TALLAW, UPTUMT |
| NSW_G2 | MW output (Positive) from the following generators: HUMEPS (connected to its VIC or NSW connection point), URANQU |
| NSW Sth East Gen | Generation in south eastern NSW. Values associated with this term are positive. Generation in this region: Boco Rock WF, Capital WF, Crookwell WF, Gullen Range WF, Gullen SF, Taralga WF and Woodlawn WF |
| NW_VIC_WF_cont | MW Output of Ararat WF, Bulgana WF, Crowlands WF, Waubra WF and Murra Warra WF. Values associated with this term are positive |
| Upper_NW_VIC_Gen_MW | Sum of generation for Kerang SF, Kiata WF, Koorangie BESS, Wemen SF, Bannerton SF, Gannawarra SF, Gannawarra Battery (gen), Karadoc SF, Gannawarra Battery (Gannawarra load is considered as negative generation) and Yatpool SF |
| NW_Vic_Gen_MW | Sum of generation in north-west Victoria. Generation in this region: Ararat WF, Bannerton SF, Bulgana WF, Challicum Hills WF, Cohuna SF, Crowlands WF, Gannawarra SF, Gannawarra Battery (gen), Karadoc SF, Kiamal SF, Kiata WF, Murra Warra WF, Waubra WF, Wemen SF, Yaloak WF, Yatpool SF and Yendon WF |
| Q3-BENDIGO 66 | MVAR output of Bendigo capacitor banks connected at 66kV. Values associated with this term are positive. |
| Q2-BURNGA 220 | MVAR output of Buronga reactor. Values associated with this term are negative |
| Q2-DENILQ_132 | MVAR output of DENILQ capacitor banks connected at 132kV. Values associated with this term are positive |
| Q3-KERANG 66 | MVAR contribution from Kerang terminal station 66 kV reactors and capacitors. Values associated with this term are negative and positive. |
| QC_SH2 | MVAR contribution from the capacitors (Values associated with caps are positive) connected at: BOMEN__33, COLEMB__33, DARLIN__33, FINLEY__33, HILLST__33, DAL_PT_132, DENILQ_132, FINLEY__66, GRIFIT__33, WAGGA1__66, WAGGA_132, WAGGA_330 |
| QC_HYTS_275kV | Nominal reactive power generation (MVAr) of the Heywood 275 kV switched capacitor. |
| QRC_SHUNTS_3 | Nominal reactive power generation (MVAr) of the Ballarat 66kV and Horsham 66 kV switched shunts and Horsham 66 kV fixed reactor |
| QC_MLTS_220kV | Nominal reactive power generation (MVAr) by Moorabool 220 kV capacitors |
| RCTS-MLK_MVAR | RCTS-MLK_MVAR MVAR flow from Redcliff to Murraylink 220kV line. Measured at Redcliff. Flow is positive from Redcliff to Murraylink. |
| RCTS_TX1-4 | Sum of MW flow on Red Cliffs 220/66 kV, 220/22 kV and 220/66/22 kV transformers. Positive value indicates power flow from HV to LV side. |
| ROTS_SVC_MVAR | MVAR output of Rowville SVC |
| SGVARS | State grid Vars, MVAR output of the shunt devices at the following locations: Ballarat (BAL-66), Bendigo (BEN_G1), Dederang (DED-220), Glenrowan (GLN-66), Horsham (HOR-66), Kerang (KER-66, KER-22), Red Cliffs (RED-66, RED-22), Shepparton (SHE_G1), Terang (TER-66). |
| Silverton WF MW | MW output from Silverton wind farm |
| Silverton WF MVAR | MVAR output from Silverton wind farm |
| SNOWY Inertia | Inertia from the Snowy area (Murray, Lower Tumut and Upper Tumut). Inertia is on a 100 MVA base (MW.sec / 100 MVA). |
| State Grid Load | Vic State Grid Load. This is the sum of the State Grid Load North (SGLN) and State Grid Load South (SGLS). |
| State Grid Load North | Vic State Grid Load north is the sum of load at the following bulk supply points: Bendigo (BETS), Fosterville (FVTS), Glenrowan (GNTS), Kerang (KGTS), Mt Beauty (MBTS), Red Cliffs (RCTS), Shepparton (SHTS), Wemen (WETS), and Wodonga (WOTS) |
| State Grid Load South | Vic State Grid Load south is the sum of load at the following bulk supply points: Ararat (ARTS), Ballarat (BATS), Horsham (HOTS), Stawell (STA) and Terang (TGTS). |
| SE_NSW_WND_SOL_GEN | Generation in South East NSW. Values associated with this term are positive. Generation in this region are Crookwell SF, Gullen Range WF, Gullen SF, Capital WF, Cullerin Range WF, Gunning WF, Taralga WF, Woodlawn WF, Walla Walla SF. |
| STH_NSW | Load in Southern NSW is the sum of customer load at the following bulk supply points: Bega 66, Cooma 66, Gadara, Munyan 33, Steple 132, Belcon 132, Causeway 132,Citest 132, Civic 132,EastLk 132, Gilmore 132, Gold Creek 132, Latham 132, Queanbeyan 66, Theodore 132, Wanniassa 132, Woden 132, Fairfax 132, Goulburn 132, Yass 66, ANM 132, Coleambally 132, Corowa 132, Darlington point 132, Deniliquin 66, Finley 66, Griffith 33, Morven 132, Mulwala 132, Murrumburrah 132, Murrumburrah 66, Wagga 66, Wagga N 132, Wagga N 66, Yanco 33, Balranald 22 |
| SW_NSW | Load in South West NSW is the sum of customer load at the following bulk supply points: Broken Hill (BKH_S1-22 and BKH-220), Gadara (GAD-11), Jounama (JOU-66), Darlington Point (DLP-132), Morven (MOR-132), Albury (ALB-132), AMN-132, Coleambally (CLY-132), Marulan (MRN-132, GOU-132), Wagga (WAN-132, WAN-66, WAW-132), Murrumburrah (MRU-66), Deniliquin (DNQ-66), Yass (YAS-66), Balranald (BRD-22), Finley (FNY-132), Griffith (GRF-132), Mulwala (MUL-132), Corowa (COR-132), and Yanco (YNC-33) |
| SW_NSW_GEN | Generation in South West NSW. Values associated with this term are positive. Generation in this region is Darlington Point SF, Coleambally SF, Limondale 1 and 2 SFs, Sunraysia SF, Finley SF, Griffith WF, Uranquinty, |
| STH_NSW_GEN | Generation in southern NSW. Values associated with this term are positive. Generation in this region is Gullen Range WF, Gullen SF, Capital WF, Cullerin Range WF, Gunning WF, Boco Rock WF, Taralga WF, Woodlawn WF, Burrinjuck Hydro, Blowering Hydro, Gadara, and Jounama Hydro Embedded generation |
| STH_NSW_WIND_SOLAR_GEN | MW output from NSW south wind and solar generation plant and Broken Hill battery output (discharging is positive and charging is negative) |
| UQT Gen | MW output from Uranquinty (UQT) Power Station. |
| U_TUMUT_Gen | MW output from Upper Tumut 1 and Upper Tumut 2 Power Station (UTSS). |
| UTUM1SC+UTUM2SC | Number of generator units operating as synchronous condensers at Upper Tumut 1 and Upper Tumut 2. |
| VIC_ASGZ2 | MW output (Positive) from the following farms: BANNER__SF, COHUNS__SF, KARADO__SF, KIAMAL__SF, Kerang SF, Koorangie BESS, WEMEN__SF, YATPOO__SF, GANAWR__SF, GANAWA_BAT |
| V_MLTS5 | MLTS 500 kV voltage (typical values between 450 and 550 kV). |
| Vic Demand | Vic MW demand (calculated as generation minus export). |
| VIC MEL LOAD pos | Load in Melbourne is the sum of customer load at the following (Zone 12) bulk supply points: Jeeralang A (JEA_G1-4), Jeeralang B (JEB_G1-3), Loy Yang A (LYA_G1-4), Loy Yang B (LYB_G1-2), Valley Power (VAL_G1), Mortlake (MRT_G1-2), Morwell (MOR_G1-3, MOW-66, MOW-22), Newport (NEW_G1), Somerton (SOM_G1-4, SEP-66), Yallourn (YPS_G1-4, YPS_T5, YPS-22), Altona (ALT-66), Richmond (RIC_G1, RIC-66, RIC-22), John Lysaght Aust. (JOH-220), Wonthaggi Diesel (WON-220), Altona Chemicals (ATC-66), Brooklyn (BRO-66, BRO-22), Brunswick (BRU-66, BRU-22), Cranbourne (CRA-66), East Rowville (EAS_G1, EAS-66), Fishermans Bend (FIS_G1), Geelong (GEE_G1, GEE-66), Heatherton (HEA_G1), Keilor (KEL_G1, KEL-66), Laverton North (LVN-66), Loy Yang (LOY-66), Malvern (MAL-66, MAL-22), Ringwood (RIN-66, RIN-22), South Morang (SOU-66), Springvale (SPR_G1, SPR-66), Tyabb (TYA-66), Templestowe (TEM_G1, TEM-66), Thomastown (THO_G1-2), West Melbourne (WML-66, WML-22), Toyota (TOY-66), Heywood (HEY-22). |
| VIC_MELB_LOAD_MW | Melbourne metropolitan region load [MW] |
| Vic to SA (Heywood) | MW transfer from Vic to SA via Heywood (measured at South East end). The interconnector direction and lines it consists of follow the NEM standard. |
| Vic to SA (Murraylink) | MW transfer from Vic to SA via Murraylink (measured at Red Cliffs end). Values associated with this term are positive for flows from Victoria to South Australia |
| Vic Demand - State Grid Load | Vic Demand (MW) minus Vic State Grid Load (SGL). |
| Vic Demand - State Grid Load - APD Load | Vic Demand (MW) minus Vic State Grid Load (SGL) minus APD load. |
| Vic Demand - State Grid Load North – APD Load | Vic Demand (MW) minus Vic State Grid Load North (SGLN) minus APD Load. |
| Vic Demand – APD Load | Vic Demand (MW) minus APD Load. |
| VIC_G1__MW | MW output (Positive) from the following generators: Note that unit should be operating as a generator. MURRAY, CLOVER, DARTMO, MKAYCK, WSTKWA, EILDON, GUTHGA |
| Vic Metro Gen | MW output from Vic metropolitan generators (Newport, Somerton, and Laverton North). |
| Vic Metro Gen Inertia | Inertia from Vic metropolitan generators (Newport, Somerton and Laverton North). Inertia is on a 100 MVA base (MW.sec / 100 MVA) as per EMS. |
| Vic Sth West Gen | MW Generation from Victorian generators in the south-west of Victoria. Generation in this region is: Elaine WF, Dundonnell WF, Macarthur WF, Hawkesdale WF, Ryan Corner WF, Moorabool WF, Mortlake PS, Morton WF, Mt Gellibrand WF, Mt Mercer WF, Oakhill WF, Portland WF, Salt Creek WF, Stockyard Hill WF and Yambuk WF |
| Vic Wind & Solar | MW Generation from Vic windfarms and solar plant (Ararat WF, Bald Hill WF, Ballarat battery, Bannerton SF, Bulgana WF, Challicum Hills WF, Crowlands WF, Elain WF, Gannawarra battery), Gannawarra SF, Hazelwood battery, Karadoc SF, Kerang SF, Kiata WF, Koorangie BESS, Macarthur WF, Hawkesdale WF, Ryan Corner WF, Girgarre WF, Wunghnu WF, Moorabool WF, Mokoan SF, Mortons Lane WF, Mount Gelibrand WF, Mount Mercer WF, Murra Warra WF, Numurkah SF, Oaklands Hill WF, Portland WF, Range Bank BESS, Salt Creek WF, Waubra WF, Wemen SF, Yaloak South WF, Yambuk WF, Yatpool SF and Yendon SF). For all batteries discharging is considered positive and charging is considered negative. |
| WAGGACap | MVAR output of Wagga Wagga capacitor banks. Values associated with this term are positive. |
| WAGGACap_66 | MVAr output of Wagga 66 kV capacitor |
| WETS Load | WETS Load Wemen (WETS) customer load (MW) |
| WETS_TX1_TX2 MW | Sum of MW flow on Wemen B1 and B2 220/66 kV transformers. Positive value indicates power flow from HV to LV side. |
| WETS_TX1_TX2 MVAR | Sum of MVAR flow on Wemen B1 and B2 220/66 kV transformers. Positive value indicates power flow from HV to LV side. |
| WKPS GEN | MW output from West Kiewa Power Station [WKPS]. |
| WOTSCap | MVAR output of Wodonga capacitor banks. Values associated with this term are positive. |
| X4_line+BRK_TX1 | Sum of MW flow of X4 line (load), measured at Broken Hill and MW flow on Broken Hill B1 and B2 220/22 kV transformers. Positive value indicates power flow from HV to LV side. |
| Q_SS_YASS | MVAR output of Yass 330 kV reactor and Yass 132 capacitors. Values associated with reactor are negative and Values associated with caps are positive. |
| YASSCap | MVAR output of Yass capacitor banks. Values associated with this term are positive. |

Glossary

This document uses many terms that have meanings defined in the National Electricity Rules (NER). The NER meanings are adopted unless otherwise specified.

| Term | Definition |
| --- | --- |
| Constraint equation | These are the mathematical representations that AEMO uses to model power system limitations and FCAS requirements in National Electricity Market Dispatch Engine (NEMDE). |
| System normal | The configuration of the power system where: All transmission elements are in service, or The network is operating in its normal network configuration |
| TNSP | Transmission Network Service Provider |

AEMO, Power System Stability Guidelines, Available at: https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/system-operations/congestion-information-resource, Viewed on: 6 October 2020.

Available at: https://www.vicgrid.com.au/transmission-planning/planning-the-energy-grid

Available at: 2025 Victorian Annual Planning Report