| Customer Connection Application Checklist Prepared by: VicGrid Version: 1.0 Effective date: November 2025 Status: Final |  |  |
| --- | --- | --- |

Important notice

This document is made available on the following basis:

Purpose

This document has been prepared by VicGrid’s team to provide guidance to Applicants about the minimum information and documents to be submitted with a connection application, to enable VicGrid to undertake its assessment under Chapter 5 of the National Electricity Rules.

Disclaimer

This document may be subsequently updated or amended.

This document does not constitute legal or business advice and should not be relied on as a substitute for obtaining detailed advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. VicGrid has made every effort to ensure the quality of the information in this document but cannot guarantee its accuracy or completeness.

Accordingly, to the maximum extent permitted by law, VicGrid and its officers, employees and consultants involved in the preparation of this document:

make no representation or warranty, express or implied, as to the currency, accuracy, reliability, or completeness of the information in this document; and

are not liable (whether by reason of negligence or otherwise) for any statements or representations in this document, or any omissions from it, or for any use or reliance on the information in it.

Copyright

© 2025 VicGrid. The material in this document is confidential and should not be disclosed without VicGrid’s permission.

Contents

1	Purpose and scope	1

1.1	Definitions and interpretation	1

1.2	Related documents	1

2	Using this document	1

3	The Checklist	2

4	Confidentiality	2

5	Additional information requests	2

6	Transmittal	2

Appendix A – Documentation completeness checklist	3

# Purpose and scope

This document contains a checklist designed to assist Applicants to ensure that an application to connect under clause 5.3.4 of the National Electricity Rules (NER) contains all relevant and necessary information to enable VicGrid’s team to complete its assessment of the Application,

The NER and the National Electricity Law (NEL) prevail over this document to the extent of any inconsistency.

## Definitions and interpretation

### Glossary

Terms defined in the NEL and the NER have the same meanings in this document unless otherwise specified.

Terms defined in the NER are intended to be identified in this document by italicising them, but failure to italicise a defined term does not affect their meaning.

The words, phrases and abbreviations in the table below have the meanings set out opposite them when used in these Procedures.

| Term | Definition |
| --- | --- |
| Applicant | A person seeking to connect a new load to the declared transmission system or modify any load connecting to the declared transmission system. |
| Application | An application to connect a load under clause 5.3.4 of the NER. |
| NEL | National Electricity Law. |
| NER | National Electricity Rules. |
| PSCAD™/EMTDC™ | Power Systems Computer Aided Design / Electromagnetic Transient with Direct Current. |
| PSS®E | Power System Simulator for Engineering. |
| SLD | Single line diagram. |

### Interpretation

This document is subject to the principles of interpretation set out in Schedule 2 of the National Electricity Law.

## Related documents

This document does not supersede or replace any other documents published by VicGrid in accordance with the NER that relate its subject matter. The list below set out these and other related documents that Applicants should be familiar with when submitting their Applications.

Customer Performance Standards template

Power System Design and Setting Data Sheets

Power System Model Guidelines

# Using this document

The Appendix contains a checklist for use by Applicants when submitting an application to connect.

The purpose of the checklist is to ensure that all necessary and relevant information and data is submitted to VicGrid to facilitate the timely assessment of the application or proposal.

# The Checklist

Applicants must complete the Documentation Completeness checklist and submit it at the appropriate time during the submission or assessment of an Application.

The listed documents and other information to be submitted is the minimum that must be submitted. Where an Applicant considers that more information would assist in the assessment of their Application, they should provide it.

# Confidentiality

VicGrid will manage the model, data and information provided by Applicants for VicGrid to assess their Application in accordance with the confidentiality requirements in clauses 5.2.4(e) and 5.3.8, of the NER.

# Additional information requests

VicGrid may request further or additional information at any time during the assessment of an application to connect and the Applicant is required to respond within the time specified by the request.

# Transmittal

Applicants must accompany any models, data or other information submitted to VicGrid with a transmittal describing the model, data or other information submitted and include a date, model number or version number, as applicable.

###### – Documentation
completeness checklist

| Requirement | Comment / file name / reference [Applicant to complete] |
| --- | --- |
| Expected load profile (24hr and annual) |  |
| Minimum and maximum demand forecast (5 years) |  |
| Proposed Performance Standards in VicGrid’s Customer Performance Standards Template. |  |
| Design reports and supporting documentation demonstrating compliance with the Technical Requirements of NER Schedule 5.3 including: Primary plant details (e.g. manufacturer, nameplate ratings, rated voltage); Protection and control design philosophy document; Fault level study report; and Power quality study report. |  |
| Single line diagrams (SLD) of the proposed installation including: Connection arrangement clearly showing the connection point, including primary electrical SLD for all HV reticulation circuits showing switching arrangements for significant plant items (including generation, UPS, large motor drives, reactive plant and harmonic filters). Protection and control details. Revenue meters and power quality meters (complete to the extent details are available). |  |
| General arrangement drawings: locating all equipment on site new or altered substations showing all exits and position of all electrical equipment. |  |
| Site specific PSS®E load flow model (.sav, .seq and .raw files) representing the customer installation including HV reticulation and load composition details. Model must include and sequence component data and connection numbers for transformer group orientation. PSS®E dynamic models (.dyr and .DLL files) for dynamic reative plant (i.e. SVC, STATCOM etc.), synchronous machines and motor drives (if available). |  |
| Power System Design and Setting Data Sheets, including all referenced documents within each data sheet (See Schedule 5.5 of the NER). |  |

| Requirement | Comment / file name / reference [Applicant to complete] |
| --- | --- |
| Note: Inapplicable data sheets should be greyed out and not removed from the document prior to VicGrid’s review and acceptance as “not applicable”. |  |
| Type test certificates for all new switchgear and transformers including instrument transformers. Please provide when available and note that these will be required prior to energisation. |  |
| Earthing details including: proposed methods of earthing cables of other equipment; plant and earth grid test certificates. Please provide when available and note that these will be required prior to energisation. |  |
| Additional information requested by VicGrid in its response to the Applicant’s connection enquiry. |  |